## QAQC (hidden)
Client:
Project: | Bellefield Title V
Job No.: | Date | Author | Self-Check Date
235950 | 4/21/25 | Libby Eastman | 4/21/25
Job No.: | Date Checked | Technical Reviewer
| 5/1/25 | Sarah Ko
| 6/30/25, 7/10/25 | Chris Campbell
Changelog
Date / Version | Sheets Revised | Editor | Description of Changes
4/30/25 | all | Sarah Ko | Tab: Table 1_Proposed NOx Emissions >> no change needed, but recommended best practice is to manage UOM conversions in a separate table instead of hard coded
| " | " | Tab: Table 2_ Revised Boiler B001 >> had question about the use of heat factors
| " | " | Tab: Table 3_ Revised Boiler B003 >> feedback on notes section
| " | " | Tab: Table 4 Revised Boiler B005 >> no comments
| " | " | Tab: Table 5_ Revised Boiler B006 >> no comments
| " | " | Tab: Table 6_ Revised Boiler B007 >> left a few comments - may need an update to the calcs
| " | " | Tab: Table 7_ No change_BoilerB008a_ >> no comments
| " | " | Tab: Table 8 EGA&BHAPs >> left feedback on formatting, notes
| " | " | Tab: Table 9_Revised Facility PTE_Su >> left a few comments. Consider the changes for consistency purposes, but they won't impact the numerical values
| " | " | Tab: Table 10 GHG_PTE >> left a few comments. Updating the GWP values will change the numbers
| Natural Gas tabs | Chris Campbell | Addressed Sarah Ko's comments - adjusted NG lb/MMscf factors based on 1050 btu/scf heat input. Lb/mmbtu factors remained the same.
| All | Chris Campbell | Removed all language regarding "proposed" and "revised" emission rates, since that was left over from the previous application and not applicable to this application.

## NO PRINT Proposed NOx Emissions (hidden)
Attachment C- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 1 - Proposed NOx RACT Maximum Potential Emission Rates
Emission ID | Proposed NOx limit (lb/MMBtu) | Maximum Heat Input Capacity (MMBtu/hr) | Fuel | Maximum Hours of Operation | Proposed Revised NOx Emission Rates |  | Current Nox limit in Title V (lb/MMBtu) | Current Permit limit (Tpy) | Difference | DO NOT PRINT
[5 empty] | lb/hr | tpy
B001 | 0.1 | 74 | Natural Gas | 8760 | 7.4 | 32.412 | 0.92 | #REF! | #REF!
B003 | 0.2 | 128 | Natural gas | 4380 | 25.6 | 56.064 | 0.63 | 167.8 | 111.736
| 0.63 | 119 | #2 fuel oil | 430 | 74.97 | 16.1185
B005 | 0.1 | 74 | Natural gas | 8760 | 7.4 | 32.412 | 0.59 | #REF! | #REF!
B006 | 0.1 | 179 | Natural gas/ | 8760 | 17.9 | 78.402 | 0.28 | 207 | 128.598
| 0.28 | 179 | # 2 fuel oil | 430 | 50.12 | 10.7758
B007 | 0.14 | 188 | Natural gas/ | 3400 | 26.32 | 44.744 | 0.2 | 38 | -6.744
| 0.2 | 188 | # 2 fuel oil | 430 | 37.6 | 8.084
B008a (No change) | 0.055 | 87 | Natural gas | 8760 | 4.785 | 20.9583
Notes:
1) Proposed NOx limits for Boilers B001, B005, B006 are the PADEP presumptive RACT limits for natural-gas-fired boilers with a heat input capacity greater than 50 MMBtu/hr (25 PA. Code, Chapter 129.97(g)(1)(i))
2) NOx limits for Boilers B003, B006 and B007 for fuel oil operation are unchanged from the current Title V Permit (ACHD Permit #0047). NOx RACT will be met through good operating practices, based on 25 PA. Code Chapter 129.97(c)(7), for emergency operation with an annual capacity factor of less than 5%.
3) Proposed NOx limits for Boilers B003 and B007 are from the case-by-case analysis in the BBP letter to ACHD regarding the NOx RACT re-evaluation request, dated March 14, 2014.
4) No emission rate changes are proposed to B008a with this application.
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Eastman, Elizabeth A. This corresponds to the proposed revisions to the latest permit application. So, we don’t need this sheet for this application Reply: Ok. I will make that change to the printout. And ensure the changes are reflected everywhere
Note on G7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consider managing the unit conversion as a separate table at the bottom, instead of hard coded into these calcs Reply: Thanks

## Table 1_ Boiler B001-32
Attachment C - Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 1 - Boiler B001 Maximum Potential Emission Rates
Natural Gas
NOx RACT emission factor | 0.1 | lb/MMBtu
Boiler B001 Operating Hours | 8760 | hours/year
Heat input capacity | 74 | MMBtu/hr
Heat Content of Natural Gas (from AP-42 factors for HAPs per Chapter 1.4) | 1050 | Btu/scf
Max allowable NG consumption | 70476.1905 | Scf/hr
Max allowable NG consumption | 617.3714 | MMscf/yr
Pollutant | lb/MMscf (AP-42) | lb/MMscf (Adjusted) | lb/MMBtu | lb/hr | tpy
PM |  |  | 0.008 | 0.592 | 2.593
PM-10 |  |  | 0.008 | 0.592 | 2.593
NOx |  |  | 0.1 | 7.4 | 32.412
CO |  |  | 0.0817 | 6.0458 | 26.4806
SO2 |  |  | 0.0006 | 0.0444 | 0.19447
VOC |  |  | 0.0054 | 0.3996 | 1.7502
Hazardous Air Pollutants (HAPs)
2 Methylnaphthalene | 2.4e-05 | 2.4706e-05 | 2.3529e-08 | 1.7412e-06 | 7.6264e-06
3-Methylchloranthrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
7,12-Dimethylbenz(a)anthracene | 1.6e-05 | 1.6471e-05 | 1.5686e-08 | 1.1608e-06 | 5.0842e-06
Acenaphthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Acenaphthylene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Anthracene | 2.4e-06 | 2.4706e-06 | 2.3529e-09 | 1.7412e-07 | 7.6264e-07
Benz(a)anthracene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Benzene | 0.0021 | 0.0021618 | 2.0588e-06 | 0.00015235 | 0.00066731
Benzo(a)pyrene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 8.7059e-08 | 3.8132e-07
Benzo(b)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Benzo(g,h,i)perylene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 8.7059e-08 | 3.8132e-07
Benzo(k)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Chrysene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Dibenzo(a,h)anthracene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 8.7059e-08 | 3.8132e-07
Dichlorobenzene | 0.0012 | 0.0012353 | 1.1765e-06 | 8.7059e-05 | 0.00038132
Fluoranthene | 3e-06 | 3.0882e-06 | 2.9412e-09 | 2.1765e-07 | 9.5329e-07
Fluorene | 2.8e-06 | 2.8824e-06 | 2.7451e-09 | 2.0314e-07 | 8.8974e-07
Formaldehyde | 0.075 | 0.077206 | 7.3529e-05 | 0.0054412 | 0.023832
Hexane | 1.8 | 1.8529 | 0.0017647 | 0.13059 | 0.57198
Indeno(1,2,3-cd)pyrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Naphthalene | 0.00061 | 0.00062794 | 5.9804e-07 | 4.4255e-05 | 0.00019384
Phenanthrene | 1.7e-05 | 1.75e-05 | 1.6667e-08 | 1.2333e-06 | 5.402e-06
Pyrene | 5e-06 | 5.1471e-06 | 4.902e-09 | 3.6275e-07 | 1.5888e-06
Toluene | 0.0034 | 0.0035 | 3.3333e-06 | 0.00024667 | 0.0010804
Total HAPs |  |  |  | 0.13657 | 0.59816
Notes:
1) The lb/MMBtu and lb/hr emission rates for PM, PM-10, CO, SO2 and VOC are unchanged from the 2018 Title V Permit (ACHD Permit #0047).
2) The NOx lb/hr emission factor is based on the heat input rating of 74 MMBtu/hr and NOx RACT limit of 0.10 lb/MMBtu,
the PADEP presumptive RACT limit in 25 PA. Code, Chapter 129.97(g)(1)(i)).
3) HAPs emission factors are based on AP-42 Chapter 1.4. However, lb/MMscf values were adjusted to reflect a 1,050 heat content
Cells in blue indicate changes in emission limits and/or proposed revisions in the permit application.

## Table 2_ Boiler B003-34
Attachment C- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 2 - Boiler B003 Maximum Potential Emission Rates
(Boiler 3 stack test results from Nov 2016)
Natural Gas | [5 empty] | Fuel Oil
NOx RACT emission factor | 0.2 | lb/MMBtu
Boiler B003 Natural Gas Operating Hours | 8760 | hours/year |  |  |  | Proposed Max Boiler B003 Fuel Oil Operating Hours |  |  | 430 | hours/year
Heat Input Capacity | 128 | MMBtu/hr |  |  |  | Heat Input Capacity |  |  | 119 | MMBtu/hr
Annual Average Heat Input Capacity | 64 | MMBtu/hr |  |  |  | Heat Content of #2 Fuel Oil for AP-42 HAPs emission factors |  |  | 0.14 | MMBtu/gallon
Allowable Boiler B003 NG Operating Hours | 4380 | hours/year
Heat Content of Natural Gas (for AP-42 factors for HAPs per Chapter 1.4) | 1050 | Btu/scf |  |  |  | Max allowable FO consumption (From Title V) |  |  | 850 | gal/hr
Max allowable NG consumption (based on max heat input capacity) | 121904.7619 | Scf/hr |  |  |  | Max allowable FO consumption |  |  | 365500 | gal/yr
Max allowable NG consumption | 533.9429 | MMscf/yr |  |  |  | Proposed Annual Capacity Factor |  |  | 4.9087 | %
Pollutant | lb/MMscf (AP-42) | lb/MMscf (Adjusted) | lb/MMBtu | lb/hr | tpy | Pollutant | lb/10^3gal | lb/MMBtu | lb/hr | tpy
PM |  |  | 0.008 | 1.024 | 2.2426 | PM |  |  | 1.78 | 0.3827
PM-10 |  |  | 0.008 | 1.024 | 2.2426 | PM-10 |  |  | 1.78 | 0.3827
NOx |  |  | 0.2 | 25.6 | 56.064 | NOx |  |  | 74.97 | 16.1185
CO |  |  | 0.0817 | 10.4576 | 22.9021 | CO |  |  | 4.25 | 0.91375
SO2 |  |  | 0.0006 | 0.0768 | 0.16819 | SO2 |  |  | 103.61 | 22.2762
VOC |  |  | 0.0054 | 0.6912 | 1.5137 | VOC |  |  | 0.29 | 0.06235
Hazardous Air Pollutants (HAPs) | [5 empty] | Hazardous Air Pollutants (HAPs)
2 Methylnaphthalene | 2.4e-05 | 2.4706e-05 | 2.3529e-08 | 3.0118e-06 | 6.5958e-06 | Benzene | 0.000214 | 1.5286e-06 | 0.0001819 | 3.9109e-05
3-Methylchloranthrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | Ethylbenzene | 6.36e-05 | 4.5429e-07 | 5.406e-05 | 1.1623e-05
7,12-Dimethylbenz(a)anthracene | 1.6e-05 | 1.6471e-05 | 1.5686e-08 | 2.0078e-06 | 4.3972e-06 | Formaldehyde | 0.033 | 0.00023571 | 0.02805 | 0.0060307
Acenaphthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | Naphthalene | 0.00113 | 8.0714e-06 | 0.0009605 | 0.00020651
Acenaphthylene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | 1,1,1-Trichloroethane | 0.000236 | 1.6857e-06 | 0.0002006 | 4.3129e-05
Anthracene | 2.4e-06 | 2.4706e-06 | 2.3529e-09 | 3.0118e-07 | 6.5958e-07 | Toluene | 0.0062 | 4.4286e-05 | 0.00527 | 0.001133
Benz(a)anthracene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | o-Xylene | 0.000109 | 7.7857e-07 | 9.265e-05 | 1.992e-05
Benzene | 0.0021 | 0.0021618 | 2.0588e-06 | 0.00026353 | 0.00057713 | Acenaphthene | 2.11e-05 | 1.5071e-07 | 1.7935e-05 | 3.856e-06
Benzo(a)pyrene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 1.5059e-07 | 3.2979e-07 | Acenaphthylene | 2.53e-07 | 1.8071e-09 | 2.1505e-07 | 4.6236e-08
Benzo(b)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | Anthracene | 1.22e-06 | 8.7143e-09 | 1.037e-06 | 2.2296e-07
Benzo(g,h,i)perylene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 1.5059e-07 | 3.2979e-07 | Benz(a)anthracene | 4.01e-06 | 2.8643e-08 | 3.4085e-06 | 7.3283e-07
Benzo(k)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | Benzo(b,k)fluoranthene | 1.48e-06 | 1.0571e-08 | 1.258e-06 | 2.7047e-07
Chrysene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | Benzo(g,h,i)perylene | 2.26e-06 | 1.6143e-08 | 1.921e-06 | 4.1302e-07
Dibenzo(a,h)anthracene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 1.5059e-07 | 3.2979e-07 | Chrysene | 2.38e-06 | 1.7e-08 | 2.023e-06 | 4.3494e-07
Dichlorobenzene | 0.0012 | 0.0012353 | 1.1765e-06 | 0.00015059 | 0.00032979 | Dibenzo(a,h) anthracene | 1.67e-06 | 1.1929e-08 | 1.4195e-06 | 3.0519e-07
Fluoranthene | 3e-06 | 3.0882e-06 | 2.9412e-09 | 3.7647e-07 | 8.2447e-07 | Fluoranthene | 4.84e-06 | 3.4571e-08 | 4.114e-06 | 8.8451e-07
Fluorene | 2.8e-06 | 2.8824e-06 | 2.7451e-09 | 3.5137e-07 | 7.6951e-07 | Fluorene | 4.47e-06 | 3.1929e-08 | 3.7995e-06 | 8.1689e-07
Formaldehyde | 0.075 | 0.077206 | 7.3529e-05 | 0.0094118 | 0.020612 | Indo(1,2,3-cd)pyrene | 2.14e-06 | 1.5286e-08 | 1.819e-06 | 3.9108e-07
Hexane | 1.8 | 1.8529 | 0.0017647 | 0.22588 | 0.49468 | Phenanthrene | 1.05e-05 | 7.5e-08 | 8.925e-06 | 1.9189e-06
Indeno(1,2,3-cd)pyrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 2.2588e-07 | 4.9468e-07 | Pyrene | 4.25e-06 | 3.0357e-08 | 3.6125e-06 | 7.7669e-07
Naphthalene | 0.00061 | 0.00062794 | 5.9804e-07 | 7.6549e-05 | 0.00016764 | OCDD | 3.1e-09 | 2.2143e-11 | 2.635e-09 | 5.6653e-10
Phenanthrene | 1.7e-05 | 1.75e-05 | 1.6667e-08 | 2.1333e-06 | 4.672e-06 | Antimony | 0.00525 | 3.75e-05 | 0.0044625 | 0.00095944
Pyrene | 5e-06 | 5.1471e-06 | 4.902e-09 | 6.2745e-07 | 1.3741e-06 | Arsenic | 0.00132 | 9.4286e-06 | 0.001122 | 0.00024123
Toluene | 0.0034 | 0.0035 | 3.3333e-06 | 0.00042667 | 0.0009344 | Beryllium | 2.78e-05 | 1.9857e-07 | 2.363e-05 | 5.0804e-06
Total HAPs |  |  |  | 0.23622 | 0.51733 | Cadmium | 0.000398 | 2.8429e-06 | 0.0003383 | 7.2735e-05
[6 empty] | Chromium | 0.000845 | 6.0357e-06 | 0.00071825 | 0.00015442
[6 empty] | Cobalt | 0.00602 | 4.3e-05 | 0.005117 | 0.0011002
[6 empty] | Manganese | 0.003 | 2.1429e-05 | 0.00255 | 0.00054825
[6 empty] | Mercury | 0.000113 | 8.0714e-07 | 9.605e-05 | 2.0651e-05
[6 empty] | Nickel | 0.0845 | 0.00060357 | 0.071825 | 0.015442
[6 empty] | Selenium | 0.000683 | 4.8786e-06 | 0.00058055 | 0.00012482
[6 empty] | Total HAPs |  |  | 0.12169 | 0.01868
Notes:
1) The lb/MMBtu emission rates for PM, PM-10, CO, SO2 and VOC are unchanged from the 2018 Title V Permit (ACHD Permit #0047).
2) The NOx lb/hr emission factor is based on the heat input rating of 128 MMBtu/hr with a 50% annual capacity restriction, and a NOx limit of 0.20
lb/MMBtu from the case-by-case analysis in the BBP letter to ACHD regarding the NOx RACT re-evaluation request, dated March 14, 2014.
3) The fuel oil operation lb/hr emission factors for PM, PM-10, NOx, CO , SO2 and VOC are unchanged from the 2018Title V Permit (ACHD Permit #0047).
4) HAPs emission factors for NG and #2 Fuel Oil are based on AP-42 Chapter 1.4 and Chapter 1.3, respectively. However, NG lb/MMscf values were adjusted to reflect a 1,050 heat content
5) This table presents individual emissions limits based on fuel use. The combined annual emission limits for this boiler is shown in Table 8 based on worst case scenario operation of boiler operating at 8760/2=4380 hours NG operation + 430 hours of fuel oil operation.
Cells in blue indicate changes in emission limits and/or proposed revision in the permit applications.

## Table 3_Boiler B005-38
Attachment C- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 3 - Boiler B005 Maximum Potential Emission Rates
Natural Gas
NOx RACT emission factor | 0.1 | lb/MMBtu
Boiler B005 Operating Hours | 8760 | hours/year
Heat input capacity | 74 | MMBtu/hr
Heat Content of Natural Gas (for AP-42 factors for HAPs per Chapter 1.4) | 1050 | Btu/scf
Max allowable NG consumption | 70476.1905 | Scf/hr
Max allowable NG consumption | 617.3714 | MMscf/yr
Pollutant | lb/MMscf (AP-42) | lb/MMscf (Adjusted) | lb/MMBtu | lb/hr | tpy
PM |  |  | 0.008 | 0.592 | 2.593
PM-10 |  |  | 0.008 | 0.592 | 2.593
NOx |  |  | 0.1 | 7.4 | 32.412
CO |  |  | 0.0817 | 6.0458 | 26.4806
SO2 |  |  | 0.0006 | 0.0444 | 0.19447
VOC |  |  | 0.0054 | 0.3996 | 1.7502
Hazardous Air Pollutants (HAPs)
2 Methylnaphthalene | 2.4e-05 | 2.4706e-05 | 2.3529e-08 | 1.7412e-06 | 7.6264e-06
3-Methylchloranthrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
7,12-Dimethylbenz(a)anthracene | 1.6e-05 | 1.6471e-05 | 1.5686e-08 | 1.1608e-06 | 5.0842e-06
Acenaphthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Acenaphthylene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Anthracene | 2.4e-06 | 2.4706e-06 | 2.3529e-09 | 1.7412e-07 | 7.6264e-07
Benz(a)anthracene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Benzene | 0.0021 | 0.0021618 | 2.0588e-06 | 0.00015235 | 0.00066731
Benzo(a)pyrene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 8.7059e-08 | 3.8132e-07
Benzo(b)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Benzo(g,h,i)perylene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 8.7059e-08 | 3.8132e-07
Benzo(k)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Chrysene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Dibenzo(a,h)anthracene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 8.7059e-08 | 3.8132e-07
Dichlorobenzene | 0.0012 | 0.0012353 | 1.1765e-06 | 8.7059e-05 | 0.00038132
Fluoranthene | 3e-06 | 3.0882e-06 | 2.9412e-09 | 2.1765e-07 | 9.5329e-07
Fluorene | 2.8e-06 | 2.8824e-06 | 2.7451e-09 | 2.0314e-07 | 8.8974e-07
Formaldehyde | 0.075 | 0.077206 | 7.3529e-05 | 0.0054412 | 0.023832
Hexane | 1.8 | 1.8529 | 0.0017647 | 0.13059 | 0.57198
Indeno(1,2,3-cd)pyrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 1.3059e-07 | 5.7198e-07
Naphthalene | 0.00061 | 0.00062794 | 5.9804e-07 | 4.4255e-05 | 0.00019384
Phenanthrene | 1.7e-05 | 1.75e-05 | 1.6667e-08 | 1.2333e-06 | 5.402e-06
Pyrene | 5e-06 | 5.1471e-06 | 4.902e-09 | 3.6275e-07 | 1.5888e-06
Toluene | 0.0034 | 0.0035 | 3.3333e-06 | 0.00024667 | 0.0010804
Total HAPs |  |  |  | 0.13657 | 0.59816
Notes:
1) The lb/MMBtu and lb/hr emission rates for PM, PM-10, CO, SO2 and VOC are unchanged from the 2018 Title V Permit (ACHD Permit #0047).
2) The NOx lb/hr emission factor is based on the heat input rating of 74 MMBtu/hr and NOx RACT limit of 0.10 lb/MMBtu,
the PADEP presumptive RACT limit in 25 PA. Code, Chapter 129.97(g)(1)(i)).
3) HAPs emission factors are based on AP-42 Chapter 1.4. However, lb/MMscf values were adjusted to reflect a 1,050 heat content
Cells in blue indicate changes in emission limits and/or proposed revisions in the permit applications.

## Table 4_ Boiler B006 39-40
Attachment C - Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 4 - Boiler B006 Maximum Potential Emission Rates
(Boiler 3 stack test results from Nov 2016)
Natural Gas | [5 empty] | Fuel Oil
NOx RACT emission factor | 0.1 | lb/MMBtu
Boiler B006 Operating Hours | 8760 | hours/year |  |  |  | Boiler B006 Fuel Oil Operating Hours |  |  | 430 | hours/year
Heat input capacity | 179 | MMBtu/hr |  |  |  | Heat Input Capacity |  |  | 179 | MMBtu/hr
Heat Content of Natural Gas (for AP-42 factors for HAPs per Chapter 1.4) | 1050 | Btu/scf |  |  |  | Heat Content of #2 Fuel Oil |  |  | 0.14 | MMBtu/gallon
Max allowable NG consumption | 170476.1905 | Scf/hr
Max allowable NG consumption | 1493.3714 | MMscf/yr |  |  |  | Max allowable FO consumption (From Title V) |  |  | 1280 | gal/hr
[6 empty] | Max allowable FO consumption |  |  | 550400 | gal/yr
[6 empty] | Annual Capacity Factor |  |  | 4.9087 | %
Pollutant | lb/MMscf (AP-42) | lb/MMscf (Adjusted) | lb/MMBtu | lb/hr | tpy | Pollutant | lb/10^3gal | lb/MMBtu | lb/hr | tpy
PM |  |  | 0.008 | 1.432 | 6.2722 | PM |  |  | 2.69 | 0.57835
PM-10 |  |  | 0.008 | 1.432 | 6.2722 | PM-10 |  |  | 2.69 | 0.57835
NOx |  |  | 0.1 | 17.9 | 78.402 | NOx |  |  | 50.12 | 10.7758
CO |  |  | 0.0817 | 14.6243 | 64.0544 | CO |  |  | 6.39 | 1.3739
SO2 |  |  | 0.0006 | 0.1074 | 0.47041 | SO2 |  |  | 147.2 | 31.648
VOC |  |  | 0.0054 | 0.9666 | 4.2337 | VOC |  |  | 14.68 | 3.1562
Hazardous Air Pollutants (HAPs) | [5 empty] | Hazardous Air Pollutants (HAPs)
2 Methylnaphthalene | 2.4e-05 | 2.4706e-05 | 2.3529e-08 | 4.2118e-06 | 1.8448e-05 | Benzene | 0.000214 | 1.5286e-06 | 0.00027361 | 5.8827e-05
3-Methylchloranthrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | Ethylbenzene | 6.36e-05 | 4.5429e-07 | 8.1317e-05 | 1.7483e-05
7,12-Dimethylbenz(a)anthracene | 1.6e-05 | 1.6471e-05 | 1.5686e-08 | 2.8078e-06 | 1.2298e-05 | Formaldehyde | 0.033 | 0.00023571 | 0.042193 | 0.0090715
Acenaphthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | Naphthalene | 0.00113 | 8.0714e-06 | 0.0014448 | 0.00031063
Acenaphthylene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | 1,1,1-Trichloroethane | 0.000236 | 1.6857e-06 | 0.00030174 | 6.4875e-05
Anthracene | 2.4e-06 | 2.4706e-06 | 2.3529e-09 | 4.2118e-07 | 1.8448e-06 | Toluene | 0.0062 | 4.4286e-05 | 0.0079271 | 0.0017043
Benz(a)anthracene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | o-Xylene | 0.000109 | 7.7857e-07 | 0.00013936 | 2.9963e-05
Benzene | 0.0021 | 0.0021618 | 2.0588e-06 | 0.00036853 | 0.0016142 | Acenaphthene | 2.11e-05 | 1.5071e-07 | 2.6978e-05 | 5.8002e-06
Benzo(a)pyrene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 2.1059e-07 | 9.2238e-07 | Acenaphthylene | 2.53e-07 | 1.8071e-09 | 3.2348e-07 | 6.9548e-08
Benzo(b)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | Anthracene | 1.22e-06 | 8.7143e-09 | 1.5599e-06 | 3.3537e-07
Benzo(g,h,i)perylene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 2.1059e-07 | 9.2238e-07 | Benz(a)anthracene | 4.01e-06 | 2.8643e-08 | 5.1271e-06 | 1.1023e-06
Benzo(k)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | Benzo(b,k)fluoranthene | 1.48e-06 | 1.0571e-08 | 1.8923e-06 | 4.0684e-07
Chrysene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | Benzo(g,h,i)perylene | 2.26e-06 | 1.6143e-08 | 2.8896e-06 | 6.2126e-07
Dibenzo(a,h)anthracene | 1.2e-06 | 1.2353e-06 | 1.1765e-09 | 2.1059e-07 | 9.2238e-07 | Chrysene | 2.38e-06 | 1.7e-08 | 3.043e-06 | 6.5424e-07
Dichlorobenzene | 0.0012 | 0.0012353 | 1.1765e-06 | 0.00021059 | 0.00092238 | Dibenzo(a,h) anthracene | 1.67e-06 | 1.1929e-08 | 2.1352e-06 | 4.5907e-07
Fluoranthene | 3e-06 | 3.0882e-06 | 2.9412e-09 | 5.2647e-07 | 2.3059e-06 | Fluoranthene | 4.84e-06 | 3.4571e-08 | 6.1883e-06 | 1.3305e-06
Fluorene | 2.8e-06 | 2.8824e-06 | 2.7451e-09 | 4.9137e-07 | 2.1522e-06 | Fluorene | 4.47e-06 | 3.1929e-08 | 5.7152e-06 | 1.2288e-06
Formaldehyde | 0.075 | 0.077206 | 7.3529e-05 | 0.013162 | 0.057649 | Indo(1,2,3-cd)pyrene | 2.14e-06 | 1.5286e-08 | 2.7361e-06 | 5.8827e-07
Hexane | 1.8 | 1.8529 | 0.0017647 | 0.31588 | 1.3836 | Phenanthrene | 1.05e-05 | 7.5e-08 | 1.3425e-05 | 2.8864e-06
Indeno(1,2,3-cd)pyrene | 1.8e-06 | 1.8529e-06 | 1.7647e-09 | 3.1588e-07 | 1.3836e-06 | Pyrene | 4.25e-06 | 3.0357e-08 | 5.4339e-06 | 1.1683e-06
Naphthalene | 0.00061 | 0.00062794 | 5.9804e-07 | 0.00010705 | 0.00046887 | OCDD | 3.1e-09 | 2.2143e-11 | 3.9636e-09 | 8.5217e-10
Phenanthrene | 1.7e-05 | 1.75e-05 | 1.6667e-08 | 2.9833e-06 | 1.3067e-05 | Antimony | 0.00525 | 3.75e-05 | 0.0067125 | 0.0014432
Pyrene | 5e-06 | 5.1471e-06 | 4.902e-09 | 8.7745e-07 | 3.8432e-06 | Arsenic | 0.00132 | 9.4286e-06 | 0.0016877 | 0.00036286
Toluene | 0.0034 | 0.0035 | 3.3333e-06 | 0.00059667 | 0.0026134 | Beryllium | 2.78e-05 | 1.9857e-07 | 3.5544e-05 | 7.642e-06
Total HAPs |  |  |  | 0.33034 | 1.4469 | Cadmium | 0.000398 | 2.8429e-06 | 0.00050887 | 0.00010941
[6 empty] | Chromium | 0.000845 | 6.0357e-06 | 0.0010804 | 0.00023228
[6 empty] | Cobalt | 0.00602 | 4.3e-05 | 0.007697 | 0.0016549
[6 empty] | Manganese | 0.003 | 2.1429e-05 | 0.0038357 | 0.00082468
[6 empty] | Mercury | 0.000113 | 8.0714e-07 | 0.00014448 | 3.1063e-05
[6 empty] | Nickel | 0.0845 | 0.00060357 | 0.10804 | 0.023228
[6 empty] | Selenium | 0.000683 | 4.8786e-06 | 0.00087326 | 0.00018775
[6 empty] | Total HAPs |  |  | 0.18305 | 0.028099
Notes:
1) The lb/MMBtu emission rates for PM, PM-10, CO, SO2 and VOC are unchanged from the2018 Title V Permit (ACHD Permit #0047).
2) The NOx lb/hr emission factor is based on the heat input rating of 179 MMBtu/hr and NOx RACT limit of 0.10 lb/MMBtu,
the PADEP presumptive RACT limit in 25 PA. Code, Chapter 129.97(g)(1)(i)).
3) The fuel oil operation lb/hr emission factors for PM, PM-10, NOx, CO , SO2 and VOC are unchanged from the current Title V Permit (ACHD Permit #0047).
4) HAPs emission factors for NG and #2 Fuel Oil are based on AP-42 Chapter 1.4 and Chapter 1.3, respectively. However, NG lb/MMscf values were adjusted to reflect a 1,050 heat content
5) This table presents individual emissions limits based on fuel use. The combined annual emission limits for this boiler is shown in Table 8 based on worst case scenario operation of boiler operating at 8760-430 = 8330 hours +430 hours of fuel oil operation.
Cells in blue indicate changes in emission limits and/or proposed revisions in the permit application.

## Table 6_ Revised Boiler B007_de (hidden)
Appendix D - Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 6 - Revised Boiler B007 Potential to Emit Emissions
OPTION 1
Natural Gas | [5 empty] | Fuel Oil
Proposed NOx emission factor |  | 0.14 | lb/MMBtu |  |  | Proposed NOx emission factor |  | 0.2 | lb/MMBtu
Proposed Boiler B007 Operating Hours |  | 3400 | hours/year |  |  | Proposed Boiler B007 Operating Hours |  | 430 | hours/year
Heat input capacity |  | 188 | MMBtu/hr |  |  | Heat Input Capacity |  | 188 | MMBtu/hr
Pollutant | lb/MMBtu | lb/hr | tpy |  |  | Pollutant | lb/MMBtu | lb/hr | tpy
PM | 0.008 | 1.504 | 2.5568 |  |  | PM | 0.015 | 2.82 | 0.6063
PM-10 | 0.008 | 1.504 | 2.5568 |  |  | PM-10 | 0.015 | 2.82 | 0.6063
NOx | 0.14 | 26.32 | 44.744 |  |  | NOx | 0.2 | 37.6 | 8.084
CO | 0.082 | 15.416 | 26.2072 |  |  | CO | 0.0355 | 6.674 | 1.4349
SO2 | 0.0006 | 0.1128 | 0.19176 |  |  | SO2 | 0.821 | 154.348 | 33.1848
VOC | 0.0054 | 1.0152 | 1.7258 |  |  | VOC | 0.082 | 15.416 | 3.3144
Notes:
1)The lb/hr emission factors for PM, PM-10, CO, SO2 and VOC are obtained from the current Title V report.
2) The NOx lb/hr emission factor is based on the heat input rating of 188 MMBtu/hr and NOx limit of 0.137 lb/MMBtu as per proposed NOx RACT re-evaluation letter dated March 14, 2014.
Greenhouse Gas Emissions
Emission Unit | Fuel | Heat input Capacity (MMBtu/hr) | Maximum Operating Hours | Max rated capacity (MMBtu/yr) | GHG Emissions (MT/yr) |  |  | Total GHG Emissions (MT/yr) | GHG Emissions (tons/yr |  |  | Total GHG Emissions (tpy) | GHG Emissions (MTCO2e/yr) |  |  | Total GHG Emissions (MTCO2e/yr)
[5 empty] | CO2 | CH4 | N2O |  | CO2 | CH4 | N2O |  | CO2 | CH4 | N2O
B007 | Natural Gas | 188 | 8760 | 1646880 | 87383.4528 | 1.6469 | 0.16469 | 87385.2644 | 96323.6539 | 1.8154 | 0.18154 | 96325.6508 | 87383.4528 | 41.172 | 49.077 | 87473.7018
| Fuel Oil | 188 | 500 | 94000 | 4987.64 | 0.094 | 0.0094 | 4987.7434 | 5497.9254 | 0.10362 | 0.010362 | 5498.0394 | 4987.64 | 2.35 | 2.8012 | 4992.7912
92466.493
Global Warming Potential (40 CFR 98 Subpart A Table A-1)
CO2 | 1
CH4 | 25
N2O | 298
Natural Gas Emission Factors
CO2 | 53.06 | kg/MMBtu
CH4 | 0.001 | kg/MMBtu
N2O | 0.0001 | kg/MMBtu
Diesel Emission Factors
CO2 | 73.96 | kg/MMBtu
CH4 | 0.003 | kg/MMBtu
N2O | 0.0006 | kg/MMBtu
Note: Emission Factors obtained from 40 CFR 98 Subpart C Tables C-1 and C-2.
1 Metric Ton | 1000 | kg
1 Metric Ton | 1.1023 | ton
Note on H14: Shah, Disha: Should this be the same as NG boiler # 7 NOX limit

## Table 5_ Boiler B007 42-43
Attachment C- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 5 - Boiler B007 Maximum Potential Emission Rates
(Boiler 3 stack test results from Nov 2016)
Natural Gas | [5 empty] | Fuel Oil
NOx RACT emission factor | 0.14 | lb/MMBtu |  |  |  | Max allowable fuel consumption |  |  | 1340 | gal/hr
Proposed Boiler B007 Operating Hours | 3400 | hours/year |  |  |  | Boiler B007 Fuel Oil Operating Hours |  |  | 430 | hours/year
Heat input capacity | 188 | MMBtu/hr |  |  |  | Heat Input Capacity |  |  | 188 | MMBtu/hr
Heat Content of Natural Gas (for AP-42 factors for HAPs per Chapter 1.4) | 1050 | Btu/scf |  |  |  | Heat Content of #2 Fuel Oil |  |  | 0.14 | MMBtu/gallon
Annual Capacity Factor | 0.39 | (or 39%) |  |  |  | Annual Capacity Factor |  |  | 4.9087 | %
Max allowable NG consumption | 179047.619 | Scf/hr
Max allowable NG consumption | 608.7619 | MMscf/yr |  |  |  | Max allowable FO consumption (from Title V permit) |  |  | 1340 | gal/hr
[6 empty] | Max allowable FO consumption |  |  | 576200 | gal/yr
Pollutant | lb/MMscf (AP-42) | lb/MMscf (Adjusted) | lb/MMBtu | lb/hr | tpy | Pollutant | lb/10^3gal | lb/MMBtu | lb/hr | tpy
PM |  |  | 0.008 | 1.504 | 2.5568 | PM |  |  | 2.82 | 0.6063
PM-10 |  |  | 0.008 | 1.504 | 2.5568 | PM-10 |  |  | 2.82 | 0.6063
NOx |  |  | 0.14 | 26.32 | 44.744 | NOx |  |  | 37.6 | 8.084
CO |  |  | 0.0817 | 15.3596 | 26.1113 | CO |  |  | 7.24 | 1.5566
SO2 |  |  | 0.0006 | 0.1128 | 0.19176 | SO2 |  |  | 153.54 | 33.0111
VOC |  |  | 0.0054 | 1.0152 | 1.7258 | VOC |  |  | 0.46 | 0.0989
Hazardous Air Pollutants (HAPs) | [5 empty] | Hazardous Air Pollutants (HAPs)
2 Methylnaphthalene | 2.4e-05 | 2.4706e-05 | 2.2857e-08 | 4.2971e-06 | 7.3051e-06 | Benzene | 0.000214 | 1.5286e-06 | 0.00028737 | 6.1785e-05
3-Methylchloranthrene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | Ethylbenzene | 6.36e-05 | 4.5429e-07 | 8.5406e-05 | 1.8362e-05
7,12-Dimethylbenz(a)anthracene | 1.6e-05 | 1.6471e-05 | 1.5238e-08 | 2.8648e-06 | 4.8701e-06 | Formaldehyde | 0.033 | 0.00023571 | 0.044314 | 0.0095276
Acenaphthene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | Naphthalene | 0.00113 | 8.0714e-06 | 0.0015174 | 0.00032625
Acenaphthylene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | 1,1,1-Trichloroethane | 0.000236 | 1.6857e-06 | 0.00031691 | 6.8137e-05
Anthracene | 2.4e-06 | 2.4706e-06 | 2.2857e-09 | 4.2971e-07 | 7.3051e-07 | Toluene | 0.0062 | 4.4286e-05 | 0.0083257 | 0.00179
Benz(a)anthracene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | o-Xylene | 0.000109 | 7.7857e-07 | 0.00014637 | 3.147e-05
Benzene | 0.0021 | 0.0021618 | 2e-06 | 0.000376 | 0.0006392 | Acenaphthene | 2.11e-05 | 1.5071e-07 | 2.8334e-05 | 6.0919e-06
Benzo(a)pyrene | 1.2e-06 | 1.2353e-06 | 1.1429e-09 | 2.1486e-07 | 3.6526e-07 | Acenaphthylene | 2.53e-07 | 1.8071e-09 | 3.3974e-07 | 7.3045e-08
Benzo(b)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | Anthracene | 1.22e-06 | 8.7143e-09 | 1.6383e-06 | 3.5223e-07
Benzo(g,h,i)perylene | 1.2e-06 | 1.2353e-06 | 1.1429e-09 | 2.1486e-07 | 3.6526e-07 | Benz(a)anthracene | 4.01e-06 | 2.8643e-08 | 5.3849e-06 | 1.1577e-06
Benzo(k)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | Benzo(b,k)fluoranthene | 1.48e-06 | 1.0571e-08 | 1.9874e-06 | 4.273e-07
Chrysene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | Benzo(g,h,i)perylene | 2.26e-06 | 1.6143e-08 | 3.0349e-06 | 6.5249e-07
Dibenzo(a,h)anthracene | 1.2e-06 | 1.2353e-06 | 1.1429e-09 | 2.1486e-07 | 3.6526e-07 | Chrysene | 2.38e-06 | 1.7e-08 | 3.196e-06 | 6.8714e-07
Dichlorobenzene | 0.0012 | 0.0012353 | 1.1429e-06 | 0.00021486 | 0.00036526 | Dibenzo(a,h) anthracene | 1.67e-06 | 1.1929e-08 | 2.2426e-06 | 4.8215e-07
Fluoranthene | 3e-06 | 3.0882e-06 | 2.8571e-09 | 5.3714e-07 | 9.1314e-07 | Fluoranthene | 4.84e-06 | 3.4571e-08 | 6.4994e-06 | 1.3974e-06
Fluorene | 2.8e-06 | 2.8824e-06 | 2.6667e-09 | 5.0133e-07 | 8.5227e-07 | Fluorene | 4.47e-06 | 3.1929e-08 | 6.0026e-06 | 1.2906e-06
Formaldehyde | 0.075 | 0.077206 | 7.1429e-05 | 0.013429 | 0.022829 | Indo(1,2,3-cd)pyrene | 2.14e-06 | 1.5286e-08 | 2.8737e-06 | 6.1785e-07
Hexane | 1.8 | 1.8529 | 0.0017143 | 0.32229 | 0.54789 | Phenanthrene | 1.05e-05 | 7.5e-08 | 1.41e-05 | 3.0315e-06
Indeno(1,2,3-cd)pyrene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 3.2229e-07 | 5.4789e-07 | Pyrene | 4.25e-06 | 3.0357e-08 | 5.7071e-06 | 1.227e-06
Naphthalene | 0.00061 | 0.00062794 | 5.8095e-07 | 0.00010922 | 0.00018567 | OCDD | 3.1e-09 | 2.2143e-11 | 4.1629e-09 | 8.9501e-10
Phenanthrene | 1.7e-05 | 1.75e-05 | 1.619e-08 | 3.0438e-06 | 5.1745e-06 | Antimony | 0.00525 | 3.75e-05 | 0.00705 | 0.0015158
Pyrene | 5e-06 | 5.1471e-06 | 4.7619e-09 | 8.9524e-07 | 1.5219e-06 | Arsenic | 0.00132 | 9.4286e-06 | 0.0017726 | 0.0003811
Toluene | 0.0034 | 0.0035 | 3.2381e-06 | 0.00060876 | 0.0010349 | Beryllium | 2.78e-05 | 1.9857e-07 | 3.7331e-05 | 8.0263e-06
Total HAPs |  |  |  | 0.33704 | 0.57297 | Cadmium | 0.000398 | 2.8429e-06 | 0.00053446 | 0.00011491
[6 empty] | Chromium | 0.000845 | 6.0357e-06 | 0.0011347 | 0.00024396
[6 empty] | Cobalt | 0.00602 | 4.3e-05 | 0.008084 | 0.0017381
[6 empty] | Manganese | 0.003 | 2.1429e-05 | 0.0040286 | 0.00086614
[6 empty] | Mercury | 0.000113 | 8.0714e-07 | 0.00015174 | 3.2625e-05
[6 empty] | Nickel | 0.0845 | 0.00060357 | 0.11347 | 0.024396
[6 empty] | Selenium | 0.000683 | 4.8786e-06 | 0.00091717 | 0.00019719
[6 empty] | Total HAPs |  |  | 0.19226 | 0.029512
Notes:
1) The lb/MMBtu emission rates for PM, PM-10, CO, SO2 and VOC are unchanged from the 2018 Title V Permit (ACHD Permit #0047).
2) The NOx lb/hr emission factor is based on the heat input rating of 188 MMBtu/hr with a 39% annual capacity restriction, and a NOx limit of 0.14
lb/MMBtu from the case-by-case analysis in the BBP letter to ACHD regarding the NOx RACT re-evaluation request, dated March 14, 2014.
3) The fuel oil operation lb/hr emission factors for PM, PM-10, NOx, CO , SO2 and VOC are unchanged from the 2018 Title V Permit (ACHD Permit #0047).
4) HAPs emission factors for NG and #2 Fuel Oil are based on AP-42 Chapter 1.4 and Chapter 1.3, respectively. However, NG lb/MMscf values were adjusted to reflect a 1,050 heat content.
5) This table presents individual emissions limits based on fuel use. The combined annual emission limits for this boiler is shown in Table 8 based on worst-case scenario operation of boiler operating at 8760*0.39=3400 hours + 430 hours of fuel oil operation.
Cells in blue indicate changes in emission limits and/or proposed revisions in the permit application.

## Table 6_BoilerB008a-36
Attachment C- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 6 - Boiler B008a Maximum Potential Emission Rates
Natural Gas
Current NOx emission factor | 0.055 | lb/MMBtu
Boiler B008a Operating Hours | 8760 | hours/year
Heat input capacity | 87 | MMBtu/hr
Heat Content of Natural Gas (for AP-42 factors for HAPs per Chapter 1.4) | 1050 | Btu/scf
Fuel Consumption Rate | 82857.1429 | scf/hr
Pollutant | lb/MMscf (AP-42) | lb/MMscf (Adjusted) | lb/MMBtu | lb/hr | tpy
PM |  |  |  | 0.7 | 3.05
PM-10 |  |  |  | 0.7 | 3.05
NOx |  |  |  | 4.8 | 20.9
CO |  |  |  | 7.1 | 24.5
SO2 |  |  |  | 0.05 | 0.23
VOC |  |  |  | 0.47 | 2.1
Hazardous Air Pollutants (HAPs)
2 Methylnaphthalene | 2.4e-05 | 2.4706e-05 | 2.3529e-08 | 2.0471e-06 | 8.9661e-06
3-Methylchloranthrene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
7,12-Dimethylbenz(a)anthracene | 1.6e-05 | 1.6471e-05 | 1.5238e-08 | 1.3257e-06 | 5.8066e-06
Acenaphthene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Acenaphthylene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Anthracene | 2.4e-06 | 2.4706e-06 | 2.2857e-09 | 1.9886e-07 | 8.7099e-07
Benz(a)anthracene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Benzene | 0.0021 | 0.0021618 | 2e-06 | 0.000174 | 0.00076212
Benzo(a)pyrene | 1.2e-06 | 1.2353e-06 | 1.1429e-09 | 9.9429e-08 | 4.355e-07
Benzo(b)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Benzo(g,h,i)perylene | 1.2e-06 | 1.2353e-06 | 1.1429e-09 | 9.9429e-08 | 4.355e-07
Benzo(k)fluoranthene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Chrysene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Dibenzo(a,h)anthracene | 1.2e-06 | 1.2353e-06 | 1.1429e-09 | 9.9429e-08 | 4.355e-07
Dichlorobenzene | 0.0012 | 0.0012353 | 1.1429e-06 | 9.9429e-05 | 0.0004355
Fluoranthene | 3e-06 | 3.0882e-06 | 2.8571e-09 | 2.4857e-07 | 1.0887e-06
Fluorene | 2.8e-06 | 2.8824e-06 | 2.6667e-09 | 2.32e-07 | 1.0162e-06
Formaldehyde | 0.075 | 0.077206 | 7.1429e-05 | 0.0062143 | 0.027219
Hexane | 1.8 | 1.8529 | 0.0017143 | 0.14914 | 0.65325
Indeno(1,2,3-cd)pyrene | 1.8e-06 | 1.8529e-06 | 1.7143e-09 | 1.4914e-07 | 6.5325e-07
Naphthalene | 0.00061 | 0.00062794 | 5.8095e-07 | 5.0543e-05 | 0.00022138
Phenanthrene | 1.7e-05 | 1.75e-05 | 1.619e-08 | 1.4086e-06 | 6.1695e-06
Pyrene | 5e-06 | 5.1471e-06 | 4.7619e-09 | 4.1429e-07 | 1.8146e-06
Toluene | 0.0034 | 0.0035 | 3.2381e-06 | 0.00028171 | 0.0012339
Total HAPs |  |  |  | 0.15597 | 0.68315
Notes:
1) HAPs emission factors are based on AP-42 Chapter 1.4. However, lb/MMscf values were adjusted to reflect a 1,050 heat content

## Table 7 EGA&B
Attachment C- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 7 - Emergency Generators Potential to Emit Emissions
Permit Unit ID | Make Model | Fuel Type | Max Hours of Operation (hr/yr) | Electrical Power Output Rating (kW) | Engine Rating (hp)2 | Heat Input Rating (MMBtu/hr)3
Emergency Generator A | Caterpillar 3412 (500 eKW) | Diesel | 500 | 500 | 745.0111 | 5.2151
Emergency Generator B | Caterpillar 3412 (750 eKW) | Diesel | 500 | 750 | 1117.5167 | 7.8226
1EPA, in their 1995 Guidance (https://www.epa.gov/sites/production/files/2015-08/documents/emgen.pdf), believes that 500 hours is an appropriate default assumption for estimating the number of hours to calculate potential to emit from emergency generators.
2Generator engines assumed to have 10% losses, so are size 10% higher than generator electrical power rating
3Average BSFC = 7000 Btu/hp-hr, based on AP-42 Chapter 3.4 (4/25)
Emergency Generator Potential to Emit |  | EG-A |  |  | EG-B |  |  | Total
Pollutant | Emission Factors AP-42 Chapter 3 Table 3.4-1 (4/25) | Emission Rate | Potential to Emit |  | Emission Rate | Potential To Emit |  | Potential To Emit
| lb/hp-hr | (lb/hr) | lbs/year | (tons/year) | (lb/hr) | lbs/year | (tons/year) | lbs/hr | (tons/year)
PM | 0.0007 | 0.52151 | 260.7539 | 0.13038 | 0.78226 | 391.1308 | 0.19557 | 1.3038 | 0.32594
PM-10 | 0.0007 | 0.52151 | 260.7539 | 0.13038 | 0.78226 | 391.1308 | 0.19557 | 1.3038 | 0.32594
NOx | 0.024 | 17.8803 | 8940.1333 | 4.4701 | 26.8204 | 13410.2 | 6.7051 | 44.7007 | 11.1752
CO | 0.0055 | 4.0976 | 2048.7806 | 1.0244 | 6.1463 | 3073.1708 | 1.5366 | 10.2439 | 2.561
SO21 | 1.2135e-05 | 0.0090407 | 4.5204 | 0.0022602 | 0.013561 | 6.7805 | 0.0033903 | 0.022602 | 0.0056504
VOC2 | 0.000705 | 0.52523 | 262.6164 | 0.13131 | 0.78785 | 393.9246 | 0.19696 | 1.3131 | 0.32827
1SO2 calculated with Sulfur content at 15ppm, based on required sulfur content of diesel listed in EPA website: https://www.epa.gov/diesel-fuel-standards/diesel-fuel-standards-and-rulemakings
2All TOC is assumed to be VOC as a conservative assumption
HAPs from Stationary Internal Combustion Engines - Diesel
|  | EG-A |  |  | EG_B |  |  | Total
| Emission Factors | Potential to Emit |  |  | Potential to Emit |  |  | Potential to Emit
AP-42 Chapter 3
Table 3.4-3 (4/25)
Pollutant | lb/MMBtu | (lb/hr) | lbs/year | (tons/year) | (lb/hr) | lbs/year | (tons/year) | lbs/hr | (tons/year)
Benzene | 0.000776 | 0.0040469 | 2.0235 | 0.0010117 | 0.0060704 | 3.0352 | 0.0015176 | 0.010117 | 0.0025293
Toluene | 0.000281 | 0.0014654 | 0.73272 | 0.00036636 | 0.0021982 | 1.0991 | 0.00054954 | 0.0036636 | 0.0009159
Xylene | 0.000193 | 0.0010065 | 0.50326 | 0.00025163 | 0.0015098 | 0.75488 | 0.00037744 | 0.0025163 | 0.00062907
Acrolein | 7.88e-06 | 4.1095e-05 | 0.020547 | 1.0274e-05 | 6.1642e-05 | 0.030821 | 1.5411e-05 | 0.00010274 | 2.5684e-05
Formaldehyde | 7.89e-05 | 0.00041147 | 0.20573 | 0.00010287 | 0.0006172 | 0.3086 | 0.0001543 | 0.0010287 | 0.00025717
Acetaldehyde | 2.52e-05 | 0.00013142 | 0.06571 | 3.2855e-05 | 0.00019713 | 0.098565 | 4.9282e-05 | 0.00032855 | 8.2137e-05
Naphthalene | 0.00013 | 0.00067796 | 0.33898 | 0.00016949 | 0.0010169 | 0.50847 | 0.00025424 | 0.0016949 | 0.00042373
PAH | 0.000212 | 0.0011056 | 0.5528 | 0.0002764 | 0.0016584 | 0.8292 | 0.0004146 | 0.002764 | 0.000691
Total HAPs |  | 0.0088864 | 4.4432 | 0.0022216 | 0.01333 | 6.6648 | 0.0033324 | 0.022216 | 0.005554
Conversions
1.341 | hp per kW
7000 | Btu/hp-hr

## Table 8_Facility PTE_Su
Attachment C-1- Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 8 - Total Facility Potential to Emit Emissions
Table 8-1: Boiler No. 1 Emission Limitations |  |  |  |  | Table 8-2: Boiler No. 3 Emission Limitations
Pollutant | Natural Gas | Combined Annual Emission Limit |  |  | Pollutant | Natural Gas | Fuel Oil | Annual Maximum
| lb/hr | tons/year |  |  |  | lb/hr | lb/hr | tons/year
PM | 0.592 | 2.593 |  |  | PM | 1.024 | 1.78 | 2.6253
PM-10 | 0.592 | 2.593 |  |  | PM-10 | 1.024 | 1.78 | 2.6253
NOx | 7.4 | 32.412 |  |  | NOx | 25.6 | 74.97 | 72.1826
CO | 6.0458 | 26.4806 |  |  | CO | 10.4576 | 4.25 | 23.8159
SO2 | 0.0444 | 0.19447 |  |  | SO2 | 0.0768 | 103.61 | 22.4443
VOC | 0.3996 | 1.7502 |  |  | VOC | 0.6912 | 0.29 | 1.5761
HAPs | 0.13657 | 0.59816 |  |  | HAPs | 0.23622 | 0.12169 | 0.54349
Note: The combined annual emission limits for this boiler based on worst case scenario operation of boiler operating at 8760/2=4380 hours of NG operation +430 hours of fuel oil operation.
Table 8-3: Boiler No. 5 Emission Limitations |  |  |  |  | Table 8-4: Boiler No. 6 Emission Limitations
Pollutant | Natural Gas | Combined Annual Emission Limit |  |  | Pollutant | Natural Gas | Fuel Oil | Combined Annual Emission Limit
| lb/hr | tons/year |  |  |  | lb/hr | lb/hr | tons/year
PM | 0.592 | 2.593 |  |  | PM | 1.432 | 2.69 | 6.5426
PM-10 | 0.592 | 2.593 |  |  | PM-10 | 1.432 | 2.69 | 6.5426
NOx | 7.4 | 32.412 |  |  | NOx | 17.9 | 50.12 | 85.3293
CO | 6.0458 | 26.4806 |  |  | CO | 14.6243 | 6.39 | 64.0544
SO2 | 0.0444 | 0.19447 |  |  | SO2 | 0.1074 | 147.2 | 32.0953
VOC | 0.3996 | 1.7502 |  |  | VOC | 0.9666 | 14.68 | 7.1821
HAPs | 0.13657 | 0.59816 |  |  | HAPs | 0.33034 | 0.18305 | 1.4152
Note: The combined annual emission limits for this boiler is based on worst case scenario operation of boiler operating at 8760-430 = 8330 hours of NG operation +430 hours of fuel oil operation. With the exception of CO Boiler 6 emission factors that is based on boiler operating 8760 on NG since the CO lb/hr for NG is higher than for fuel oil.
Table 8-5: Boiler No. 7 Emission Limitations |  |  |  |  | Table 8-6: Facility Emissions Limitations
Pollutant | Natural Gas | Fuel Oil | Combined Annual Emission Limit |  | Pollutant | Combined Annual Emission Limit
| lb/hr | lb/hr | tons/year |  |  | tons/year
PM | 1.504 | 2.82 | 3.1631 |  | PM | 20.8929
PM-10 | 1.504 | 2.82 | 3.1631 |  | PM-10 | 20.8929
NOx | 26.32 | 37.6 | 52.828 |  | NOx | 307.239
CO | 15.3596 | 7.24 | 27.6679 |  | CO | 195.5604
SO2 | 0.1128 | 153.54 | 33.2029 |  | SO2 | 88.3671
VOC | 1.0152 | 0.46 | 1.8247 |  | VOC | 16.5117
HAPs | 0.33704 | 0.19226 | 0.6143 |  | HAPs | 4.458
Note: The combined annual emission limits for this boiler is based on worst case scenario operation of boiler operating at 3400 hours of NG operation + 430 hours of fuel oil operation. |  |  |  |  | *The facility emissions include Boiler 1, 3, 5, 6, 7, 8a, EG-A and EG-B.
Table 8-7: Boiler B008a Emission Limitations
Pollutant | Natural Gas | Combined Annual Emission Limit
| lb/hr | tons/year
PM | 0.7 | 3.05
PM-10 | 0.7 | 3.05
NOx | 4.8 | 20.9
CO | 7.1 | 24.5
SO2 | 0.05 | 0.23
VOC | 0.47 | 2.1
HAPs | 0.15597 | 0.68315
Attachment C - Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 8 - Total Facility Potential to Emit Emissions
Table 8-8: Individual Boiler Hourly Emissions based on fuel (Note: Combined annual emission limits are calculated in Table 8-1 through 8-5)
Emission ID | Emission Unit Description | Maximum Capacity (MMBtu/hr) | Fuel | Potential to Emit (Pounds per hour)
|  |  |  | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs
B001 | Boiler 1 | 74 | Natural Gas | 0.592 | 0.592 | 7.4 | 6.0458 | 0.0444 | 0.3996 | 0.13657
B003 | Boiler 3 | 128 | Natural Gas | 1.024 | 1.024 | 25.6 | 10.4576 | 0.0768 | 0.6912 | 0.23622
|  | 119 | #2 fuel oil | 1.78 | 1.78 | 74.97 | 4.25 | 103.61 | 0.29 | 0.12169
B005 | Boiler 5 | 74 | Natural Gas | 0.592 | 0.592 | 7.4 | 6.0458 | 0.0444 | 0.3996 | 0.13657
B006 | Boiler 6 | 179 | Natural gas/ | 1.432 | 1.432 | 17.9 | 14.6243 | 0.1074 | 0.9666 | 0.33034
|  | 179 | # 2 fuel oil | 2.69 | 2.69 | 50.12 | 6.39 | 147.2 | 14.68 | 0.18305
B007 | Boiler 7 | 188 | Natural gas/ | 1.504 | 1.504 | 26.32 | 15.3596 | 0.1128 | 1.0152 | 0.33704
|  | 188 | # 2 fuel oil | 2.82 | 2.82 | 37.6 | 7.24 | 153.54 | 0.46 | 0.19226
B008a | Boiler 8a | 87 | Natural Gas | 0.7 | 0.7 | 4.8 | 7.1 | 0.05 | 0.05 | 0.47
EG-A | Emergency Generator A | 5.4 | Diesel | 0.52151 | 0.52151 | 17.8803 | 4.0976 | 0.0090407 | 0.52523 | 0.0088864
EG-B | Emergency Generator B | 7.5 | Diesel | 0.78226 | 0.78226 | 26.8204 | 6.1463 | 0.013561 | 0.78785 | 0.01333
Table 8-9: Combined Annual Emissions (Potential to Emit)
Emission ID | Emission Unit Description | Combined Potential to Emit (tons/year)
|  | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs
B001 | Boiler 1 | 2.593 | 2.593 | 32.412 | 26.4806 | 0.19447 | 1.7502 | 0.59816
B003 | Boiler 3 | 2.6253 | 2.6253 | 72.1826 | 23.8159 | 22.4443 | 1.5761 | 0.54349
B005 | Boiler 5 | 2.593 | 2.593 | 32.412 | 26.4806 | 0.19447 | 1.7502 | 0.59816
B006 | Boiler 6 | 6.5426 | 6.5426 | 85.3293 | 64.0544 | 32.0953 | 7.1821 | 1.4152
B007 | Boiler 7 | 3.1631 | 3.1631 | 52.828 | 27.6679 | 33.2029 | 1.8247 | 0.6143
B008a | Boiler 8a | 3.05 | 3.05 | 20.9 | 24.5 | 0.23 | 2.1 | 0.68315
Boiler Total |  | 20.5669 | 20.5669 | 296.0639 | 192.9995 | 88.3615 | 16.1834 | 4.4525
EG-A | Emergency Generator A | 0.13038 | 0.13038 | 4.4701 | 1.0244 | 0.0022602 | 0.13131 | 0.0022216
EG-B | Emergency Generator B | 0.19557 | 0.19557 | 6.7051 | 1.5366 | 0.0033903 | 0.19696 | 0.0033324
Total Facility Emissions |  | 20.8929 | 20.8929 | 307.239 | 195.5604 | 88.3671 | 16.5117 | 4.458
*See notes above for calculation of combined emission limits for boilers 3, 6 and 7.

## A-2 (hidden)
Appendix D - Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 8 - Revised Facility Emissions
Pollutant Attainment? |  | Boiler No. 7 |  | Boiler No. 7
|  | Design Heat Input (MMBtu/hr) | Hours of operation | Future Potential Emission Factor (lb/MMBtu) (1) | Future Potential Emission Rate (lb/hr) | Future Potential Emission Rate (tons/year)
SO2(1) | Yes | 188 | 8760 | 0.00058366 | 0.10973 | 0.48061
CO (2) | Yes | 188 | 8760 | 0.0817 | 15.3596 | 67.275
NO2(2) | Yes | 188 | 8760 | 0.14 | 26.32 | 115.2816
NOX(2) | No | 188 | 8760 | 0.14 | 26.32 | 115.2816
VOC (1) | No | 188 | 8760 | 0.0053502 | 1.0058 | 4.4056
PM2.5(1) | No | 188 | 8760 | 0.008 | 1.504 | 6.5875
PM10 |  | 188 | 8760 | 0.008 |  | 6.5875
CO2 (4) | n/a | 188 | 8760 | 116.9771 | 21991.7018 | 96323.6539
CH4(4) | n/a | 188 | 8760 | 0.0022046 | 0.41447 | 1.8154
N2O (4) | n/a | 188 | 8760 | 0.00022046 | 0.041447 | 0.18154
CO2e | n/a |  |  |  |  | 96423.1363

## Form B Emissions (hidden)
Bellefield Boiler Plant - Title V Modification Application
FORM B - Part IX - Emissions
Boiler B001 burning NG | [8 empty] | Boiler B001 burning NG
lb/hr | [8 empty] | TPY
Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs
Allowable | 0.592 | 0.592 | 7.4 | 6.0458 | 0.0444 | 0.3996 | 0.13657 | - | Allowable | 2.593 | 2.593 | 32.412 | 26.4806 | 0.19447 | 1.7502 | 0.59816 | #N/A
Maximum Potential | 0.592 | 0.592 | 7.4 | 6.0458 | 0.0444 | 0.3996 | 0.13657 | #N/A | Maximum Potential | 2.593 | 2.593 | 32.412 | 26.4806 | 0.19447 | 1.7502 | 0.59816 | #N/A
Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | 0.566 | 0.141 | 6.567 | 1.72 | 0.0447 | 0.41 | 0.143 | 8937
Boiler B003 burning NG | [8 empty] | Boiler B003 burning FO | [8 empty] | Boiler B003 Combined
lb/hr | [8 empty] | lb/hr | [8 empty] | TPY
Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs
Allowable | 1.024 | 1.024 | 25.6 | 10.4576 | 0.0768 | 0.6912 | 0.23622 | #N/A | Allowable | 1.78 | 1.78 | 74.97 | 4.25 | 103.61 | 0.29 | 0.12169 | #N/A | Allowable | 2.6253 | 2.6253 | 72.1826 | 23.8159 | 22.4443 | 1.5761 | 0.54349 | #N/A
Maximum Potential | 1.024 | 1.024 | 25.6 | 10.4576 | 0.0768 | 0.6912 | 0.23622 | #N/A | Maximum Potential | 1.78 | 1.78 | 74.97 | 4.25 | 103.61 | 0.29 | 0.12169 | #N/A | Maximum Potential | 2.6253 | 2.6253 | 72.1826 | 23.8159 | 22.4443 | 1.5761 | 0.54349 | #N/A
Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | 1.621 | 0.405 | 29.611 | 4.926 | 0.128 | 1.73 | 0.41 | 25592
Boiler B005 burning NG | [8 empty] | Boiler B005 burning NG
lb/hr | [8 empty] | TPY
Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs
Allowable | 0.592 | 0.592 | 7.4 | 6.0458 | 0.0444 | 0.3996 | 0.13657 | #N/A | Allowable | 2.593 | 2.593 | 32.412 | 26.4806 | 0.19447 | 1.7502 | 0.59816 | #N/A
Maximum Potential | 0.592 | 0.592 | 7.4 | 6.0458 | 0.0444 | 0.3996 | 0.13657 | #N/A | Maximum Potential | 2.593 | 2.593 | 32.412 | 26.4806 | 0.19447 | 1.7502 | 0.59816 | #N/A
Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | 0.534 | 0.134 | 7.496 | 1.623 | 0.043 | 0.387 | 0.135 | 8433
Boiler B006 burning NG | [8 empty] | Boiler B006 burning FO | [8 empty] | Boiler B006 combined
lb/hr | [8 empty] | lb/hr | [8 empty] | TPY
Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs
Allowable | 1.432 | 1.432 | 17.9 | 14.6243 | 0.1074 | 0.9666 | 0.33034 | #N/A | Allowable | 2.69 | 2.69 | 50.12 | 6.39 | 147.2 | 14.68 | 0.18305 | #N/A | Allowable | 6.5426 | 6.5426 | 85.3293 | 64.0544 | 32.0953 | 7.1821 | 1.4152 | #N/A
Maximum Potential | 1.432 | 1.432 | 17.9 | 14.6243 | 0.1074 | 0.9666 | 0.33034 | #N/A | Maximum Potential | 2.69 | 2.69 | 50.12 | 6.39 | 147.2 | 14.68 | 0.18305 | #N/A | Maximum Potential | 6.5426 | 6.5426 | 85.3293 | 64.0544 | 32.0953 | 7.1821 | 1.4152 | #N/A
Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | 1.08 | 0.27 | 14.826 | 0.339 | 0.085 | 0.783 | 0.274 | 17090
Boiler B007 burning NG | [8 empty] | Boiler B007 burning FO | [8 empty] | Boiler B007 combined
lb/hr | [8 empty] | lb/hr | [8 empty] | TPY
Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs | Pollutant | PM | PM-10 | NOx | CO | SO2 | VOC | HAPs | GHGs
Allowable | 1.504 | 1.504 | 26.32 | 15.3596 | 0.1128 | 1.0152 | 0.33704 | #N/A | Allowable | 2.82 | 2.82 | 37.6 | 7.24 | 153.54 | 0.46 | 0.19226 | #N/A | Allowable | 3.1631 | 3.1631 | 52.828 | 27.6679 | 33.2029 | 1.8247 | 0.6143 | #N/A
Maximum Potential | 1.504 | 1.504 | 26.32 | 15.3596 | 0.1128 | 1.0152 | 0.33704 | #N/A | Maximum Potential | 2.82 | 2.82 | 37.6 | 7.24 | 153.54 | 0.46 | 0.19226 | #N/A | Maximum Potential | 3.1631 | 3.1631 | 52.828 | 27.6679 | 33.2029 | 1.8247 | 0.6143 | #N/A
Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | - | - | - | - | - | - | - | - | Actual or Estimated | 0.14 | 0.034 | 1.886 | 0.043 | 0.0107 | 0.0983 | 0.0344 | 2144
Notes:
1) Maximum Potential emissions are same as allowable for all pollutants.
2) Emissions reported in "Actual or Estimated" are from 2016 Emission Inventory submitted to PADEP.
3) GHG emissions include Methane, CO2 and N2O in tpy. The MTCO2e/yr calculations for GHG Emissions is shown in Table 10.

## Table 10 GHG_PTE (hidden)
Attachement C - Emission Calculations
Bellefield Boiler Plant, Pittsburgh
Table 9 - Greenhouse Gas Emissions - Total Facility Maximum Potential to Emit
Emission Unit | Fuel | Heat input Capacity (MMBtu/hr) | Maximum Operating Hours/yr | Max rated capacity (MMBtu/yr) | GHG Emissions (TPY) |  |  | Total GHG Emissions (tpy) | GHG Emissions (MTCO2e/yr) |  |  | Total GHG Emissions (MTCO2e/yr)
[5 empty] | CO2 | CH4 | N2O |  | CO2 | CH4 | N2O
Boiler B001 | Natural Gas | 74 | 8760 | 648240 | 37914.6639 | 0.71456 | 0.071456 | 37915.45 | 34395.6144 | 18.1507 | 17.1784 | 34430.9435
Boiler B003 | Natural Gas | 128 | 4380 | 560640 | 32791.0607 | 0.618 | 0.0618 | 32791.7405 | 29747.5584 | 15.6979 | 14.857 | 29778.1133
Boiler B005 | Natural Gas | 74 | 8760 | 648240 | 37914.6639 | 0.71456 | 0.071456 | 37915.45 | 34395.6144 | 18.1507 | 17.1784 | 34430.9435
Boiler B006 | Natural Gas | 179 | 8330 | 1491070 | 87210.6287 | 1.6436 | 0.16436 | 87212.4367 | 79116.1742 | 41.75 | 39.5134 | 79197.4375
Boiler B007 | Natural Gas | 188 | 3400 | 639200 | 37385.9268 | 0.7046 | 0.07046 | 37386.7019 | 33915.952 | 17.8976 | 16.9388 | 33950.7884
Boiler B008a | Natural Gas | 87 | 8760 | 762120 | 44575.3481 | 0.84009 | 0.084009 | 44576.2722 | 40438.0872 | 21.3394 | 20.1962 | 40479.6227
Boiler B003 | Fuel Oil (# 2 Diesel) | 119 | 430 | 51170 | 4171.7326 | 0.16922 | 0.033843 | 4171.9356 | 3784.5332 | 4.2983 | 8.136 | 3796.9675
Boiler B006 | Fuel Oil (# 2 Diesel) | 179 | 430 | 76970 | 6275.1271 | 0.25453 | 0.050907 | 6275.4326 | 5692.7012 | 6.4655 | 12.2382 | 5711.4049
Boiler B007 | Fuel Oil (# 2 Diesel) | 188 | 430 | 80840 | 6590.6363 | 0.26733 | 0.053466 | 6590.9571 | 5978.9264 | 6.7906 | 12.8536 | 5998.5705
Emergency Generator # A | Diesel | 5.4 | 500 | 2700 | 220.1227 | 0.0089287 | 0.0017857 | 220.1334 | 199.692 | 0.2268 | 0.4293 | 200.3481
Emergency Generator # B | Diesel | 5.4 | 500 | 2700 | 220.1227 | 0.0089287 | 0.0017857 | 220.1334 | 199.692 | 0.2268 | 0.4293 | 200.3481
Totals | [7 empty] | 295276.6433 | 267864.5454 | 150.9942 | 159.9484 | 268175.488
Global Warming Potential (40 CFR 98 Subpart A Table A-1) |  |  |  |  | LP Gas Emission Factors |  |  |  |  | Conversion Factors
CO2 | 1 |  |  |  | CO2 | 61.71 | kg/MMBtu |  |  | 1 Metric Ton | 1000 | kg
CH4 | 28 |  |  |  | CH4 | 0.003 | kg/MMBtu |  |  | 1 Metric Ton | 1.1023 | ton
N2O | 265 |  |  |  | N2O | 0.0006 | kg/MMBtu |  |  | 1 US Ton | 907.185 | kg
https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-98/subpart-A
Natural Gas Emission Factors |  |  |  |  | Diesel Emission Factors
CO2 | 53.06 | kg/MMBtu |  |  | CO2 | 73.96 | kg/MMBtu
CH4 | 0.001 | kg/MMBtu |  |  | CH4 | 0.003 | kg/MMBtu
N2O | 0.0001 | kg/MMBtu |  |  | N2O | 0.0006 | kg/MMBtu
Note: Emission Factors obtained from 40 CFR 98 Subpart C Tables C-1 and C-2.
Combined GHG Emissions
| CO2 | CH4 | N2O | Total | CO2 | CH4 | N2O | Total
| TPY | TPY | TPY | TPY | MTCO2e/yr | MTCO2e/yr | MTCO2e/yr | MTCO2e/yr
Boiler B001 | 37914.6639 | 0.71456 | 0.071456 | 37915.45 | 34395.6454 | 18.1507 | 17.1784 | 34430.9746
Boiler B003 | 36962.7933 | 0.78722 | 0.095643 | 36963.6761 | 33532.1219 | 19.9962 | 22.993 | 33575.1111
Boiler B005 | 37914.6639 | 0.71456 | 0.071456 | 37915.45 | 34395.6454 | 18.1507 | 17.1784 | 34430.9746
Boiler B006 | 93485.7558 | 1.8982 | 0.21527 | 93487.8693 | 84808.952 | 48.2155 | 51.7516 | 84908.9191
Boiler B007 | 43976.5631 | 0.97193 | 0.12393 | 43977.659 | 39894.9144 | 24.6882 | 29.7924 | 39949.395
Boiler B008a | 44575.3481 | 0.84009 | 0.084009 | 44576.2722 | 40438.1237 | 21.3394 | 20.1962 | 40479.6593
EG-A | 220.1227 | 0.0089287 | 0.0017857 | 220.1334 | 199.6922 | 0.2268 | 0.4293 | 200.3483
EG-B | 220.1334 | 0.0089287 | 0.0017857 | 220.1441 | 199.7019 | 0.2268 | 0.4293 | 200.358
TOTAL | 295270.0443 | 5.9444 | 0.66533 | 295276.654 | 267864.7969 | 150.9943 | 159.9486 | 268175.7398
Note: 1) The combined GHG emission limits for this boiler 3 based on worst case scenario operation of boiler 3 operating at 8760/2=4380 hours of NG operation + 430 hours of fuel oil operation.
2) The combined GHG emission limits for boiler 6 is based on worst case scenario operation of boiler 6 operating at 8760-430 = 8330 hours of NG operation +430 hours of fuel oil operation.
3) The combined GHG emission limits for the boiler 7 is based on worst case scenario operation of boiler 7 operating at 3400 hours of NG operation + 430 hours of fuel oil operation.
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add unit of measure (hr/yr) Reply: Done thanks.
Note on J5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is this data a requirement for reporting? Due to the nature of GHGs, I've really only seen GHGs reported as individual pollutants, and then CO2e. If this is not a required field for reporting, I recommend deleting it
Note on E18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For consistency, recommend referencing the emergency generator tab instead of hard coding Reply: Thank you, I referenced Table 7
Note on G24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since there is no LP being used, recommend deleting this table
Note on C26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Table A-1 is now showing the AR-5 values (CH4 is 28, N2O is 265), so these values should be updated (https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-98/subpart-A) Reply: Updated, and cited.
Note on F38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is this data a requirement for reporting? Due to the nature of GHGs, I've really only seen GHGs reported as individual pollutants, and then CO2e. If this is not a required field for reporting, I recommend deleting it

## Step 1 B7 netting 8760 (hidden)
Bellefield Boiler Plant, Pittsburgh
Title V permit modification
Step 1 Emissions Netting Calculations for Boiler 7
|  |  |  | Natural Gas | [5 empty] | Net Emissions Increase
[10 empty] | PSD | NSR
[6 empty] | Future |  | Future | Projected | Proj. Actual | Potential |  |  | PSD for attainment pollutants
|  |  | Existing Actual | Actual | Design | Potential |  | Potential | Actual | Minus | Minus | Significant |  | NSR for non-attainment pollutants (NOX, VOC and PM 2.5)
|  |  | Emission | Emission | Heat | Emission |  | Emission | Emission | Baseline | Existing | Increase
|  |  | Factor | Rate | Input | Factor | Proposed | Rate | Rate | Actual | Actual | Threshold
Pollutant | Attainment? | Case | lb/MMBtu | (tons/year) | (MMBtu/hr) | (lb/MMBtu) | Hours | (tons/year) | (tons/year) | (tons/year) | (tons/year) | (tons/year)
Did not use projected actual, used PTE instead
SO2 | Yes | Boiler 7 | 0.0006 | #REF! | 188 | 0.0006 | 8760 | 0.49406 | 0.49406 | #REF! | NA | 40
CO | Yes | Boiler 7 | 0.082 | #REF! | 188 | 0.082 | 8760 | 67.5221 | 67.5221 | #REF! | NA | 100
NO2 | Yes | Boiler 7 | 0.2 | #REF! | 188 | 0.14 | 8760 | 115.2816 | 115.2816 | #REF! | NA | 40
NOX | No | Boiler 7 | 0.2 | #REF! | 188 | 0.14 | 8760 | 115.2816 | NA | NA | #REF! | 40 | #REF!
VOC | No | Boiler 7 | 0.0054 | #REF! | 188 | 0.0054 | 8760 | 4.4466 | NA | NA | #REF! | 40
PM2.5 | No | Boiler 7 | 0.008 | #REF! | 188 | 0.008 | 8760 | 6.5875 | 6.5875 | NA | #REF! | 25
PM10 | Yes | Boiler 7 | 0.008 | #REF! | 188 | 0.008 | 8760 | 6.5875 | 6.5875 | #REF! | NA | 15
CO2 | Yes | Boiler 7 | 116.9973 | #REF! | 188 | 116.9973 | 8760 | 96340.2567 | 96340.2567 | #REF! |  | N/A
CH4 | Yes | Boiler 7 | 0.002205 | #REF! | 188 | 0.002205 | 8760 | 1.8157 | 1.8157 | #REF! |  | N/A
N2O | Yes | Boiler 7 | 0.0002205 | #REF! | 188 | 0.0002205 | 8760 | 0.18157 | 0.18157 | #REF! |  | N/A
CO2e | Yes | [8 empty] | 0 |  | 75000
Notes:
Natural gas heating value |  | 1028 | Btu/scf
Existing baseline actual fuel use |  | #REF! | MMcf/year

## Step 1 B7 netting _Case2_6320 (hidden)
Bellefield Boiler Plant, Pittsburgh
Title V permit modification
Step 1 Emissions Netting Calculations for Boiler 7
[5 empty] | Natural Gas |  |  |  |  | Net Emissions Increase
[10 empty] | PSD | NSR
[7 empty] | Future | Future | Projected | Proj. Actual | Potential |  | PSD for attainment pollutants
|  |  |  | Existing Actual | Actual | Design | Potential | Potential | Actual | Minus | Minus | Significant | NSR for non-attainment pollutants (NOX, VOC and PM 2.5)
|  |  |  | Emission | Emission | Heat | Emission | Emission | Emission | Baseline | Existing | Increase
|  |  |  | Factor | Rate | Input | Factor | Rate | Rate | Actual | Actual | Threshold
Pollutant | Attainment? | Case | Hours | lb/MMBtu | (tons/year) | (MMBtu/hr) | (lb/MMBtu) | (tons/year) | (tons/year) | (tons/year) | (tons/year) | (tons/year)
Did not use projected actual, used PTE instead
SO2 | Yes | Boiler 7 | 6320 | 0.0006 | #REF! | 188 | 0.0006 | 0.35645 | 0.35645 | #REF! | NA | 40
CO | Yes | Boiler 7 | 6320 | 0.082 | #REF! | 188 | 0.082 | 48.7146 | 48.7146 | #REF! | NA | 100
NO2 | Yes | Boiler 7 | 6320 | 0.10272 | #REF! | 188 | 0.14 | 83.1712 | 83.1712 | #REF! | NA | 40
NOX | No | Boiler 7 | 6320 | 0.10272 | #REF! | 188 | 0.14 | 83.1712 | NA | NA | #REF! | 40
VOC | No | Boiler 7 | 6320 | 0.0054 | #REF! | 188 | 0.0054 | 3.208 | NA | NA | #REF! | 40
PM2.5 | No | Boiler 7 | 6320 | 0.008 | #REF! | 188 | 0.008 | 4.7526 | 4.7526 | NA | #REF! | 25 | 38.5
PM10 | Yes | Boiler 7 | 6320 | 0.008 | #REF! | 188 | 0.008 | 4.7526 | 4.7526 | #REF! | NA | 15 | 0 | (Actual emission decrease from Boiler 3 that can be added to Boiler 7)
CO2 | Yes | Boiler 7 | 6320 |  | #REF! | 188 | 116.9973 | 69505.756 | 69505.756 |  |  | N/A | 38.5
CH4 | Yes | Boiler 7 | 6320 |  | #REF! | 188 | 0.002205 | 1.3099 | 1.3099 |  |  | N/A
N2O | Yes | Boiler 7 | 6320 |  | #REF! | 188 | 0.0002205 | 0.13099 | 0.13099 |  |  | N/A
CO2e | Yes | [10 empty] | 75000
Notes:
Natural gas heating value |  | 1028 | Btu/scf
Existing baseline actual fuel use |  | #REF! | MMcf/year
Existing Nox actual emission factor |  | 105.6 | lb/MMcf

## Boiler Emissions (hidden)
Natural Gas Emissions lb/hr | [5 empty] | Natural Gas Emissions Tpy
| B001 | B003 | B005 | B006 | B007 |  | B001 | B003 | B005 | B006 | B007
Mmbtu/hr | 74 | 128 | 74 | 179 | 188 | Operating Hours | 8760 | 500 | 8760 | 8760 | 2190 | 8760
PM | 0.59 | 1.02 | 0.59 | 1.43 | 1 | PM | 2.5842 | 0.255 | 2.5842 | 6.2634 | 1.095
PM-10 | 0.59 | 1.02 | 0.59 | 1.43 | 1 | PM-10 | 2.5842 | 0.255 | 2.5842 | 6.2634 | 1.095
NOx | #REF! | 80.64 | #REF! | #REF! | 38 | NOx | #REF! | 20.16 | #REF! | #REF! | 41.61 | 166.44 | 124.83
CO | 6.05 | 10.64 | 6.09 | 14.63 | 27 | CO | 26.499 | 2.66 | 26.6742 | 64.0794 | 29.565
SO2 | 0.04 | 0.07 | 0.04 | 0.11 | 0.1 | SO2 | 0.1752 | 0.0175 | 0.1752 | 0.4818 | 0.1095
VOC | 0.4 | 0.68 | 0.4 | 1.02 | 3.6 | VOC | 1.752 | 0.17 | 1.752 | 4.4676 | 3.942
Fuel Oil Emissions lb/hr | [5 empty] | Fuel Oil Emissions tpy
| x | B003 | x | B006 | B007 |  | x | B003 | x | B006 | B007
|  | 119 |  | 179 | 188 | Operating Hours |  | 500 |  | 500 | 500
PM |  | 1.78 |  | 2.69 | 2.82 | PM | 0 | 0.445 | 0 | 0.6725 | 0.705
PM-10 |  | 1.78 |  | 2.69 | 2.82 | PM-10 | 0 | 0.445 | 0 | 0.6725 | 0.705
NOx |  | 74.97 |  | #REF! | 37.6 | NOx | 0 | 18.7425 | 0 | #REF! | 9.4
CO |  | 4.25 |  | 6.39 | 7.24 | CO | 0 | 1.0625 | 0 | 1.5975 | 1.81
SO2 |  | 103.61 |  | 147.2 | 153.54 | SO2 | 0 | 25.9025 | 0 | 36.8 | 38.385
VOC |  | 1.4 |  | 14.68 | 0.46 | VOC | 0 | 0.35 | 0 | 3.67 | 0.115
* Highlighted in yellow is RACT limit
B

## Netting (hidden)
| Current Operating Hours | Capacity |  | Current Title V permit NOx
|  | NG | FO | NG | FO
|  | MMBtu/hr | MMBtu/hr | lb/hr | lb/hr | tpy
B003 | 8760 | 128 | 119 | 80.64 | 74.97 | 167.8
B007 | 4032 | 188 | 188 | 38 | 37.6 | 38
B003 | Annual average heat input | 64 MMBtu/hr | 560640 | MMBtu/yr
B007 | 0.2 lb/MMBtu
lb/hr
1752