## PTE Summary
|  |  | Company Name: | Brunot Island Generating Station
|  |  | Address: | Brunot Island, Pittsburhg, PA
|  |  | Title V Operating Permit: | 0056-OP25
|  |  | Reviewer: | BL
|  |  | Date: | 2024-08-13
Summary of Emissions
Potential to Emit (lb/hr)
Pollutant | Unit | [6 empty] | TOTAL
| Turbine 1A | Turbine 2A | Turbine 2B | Turbine 3 | Cooling Tower CT-1 | Diesel Starter Engine (1A-DS) | Diesel Fire Pump (FP1)
NOx | 209.4 | 11.8 | 11.8 | 11.8 | NA | 14.994 | 9.261 | 269.055
VOC | 9.22 | 3 | 3 | 3 | NA | 1.19 | 0.735 | 20.145
Lead | 0.0042 | NA | NA | NA | NA | NA | NA | 0.0042
CO | 35.5 | 40 | 40 | 40 | NA | 3.23 | 1.995 | 160.725
PM10 | 1.5 | 6.7 | 6.7 | 6.7 | 2.2278 | 0.952 | 0.588 | 25.3678
PM2.5 | 1.5 | 6.7 | 6.7 | 6.7 | 2.2278 | 0.952 | 0.588 | 25.3678
SOx | 63 | 2.6 | 2.6 | 2.6 | NA | 0.986 | 0.609 | 72.395
Ammonia | NA | 14 | 14 | 14 | NA | NA | NA | 42
Total HAP (incl. CH2O) | 0.47579 | 0.93012 | 0.93012 | 0.93012 | 0 | 0.021942 | 0.013553 | 3.3016
| Potential to Emit (tpy) | [7 empty] | RACT Notes:
Pollutant | Unit | [6 empty] | TOTAL | 2019 Permit Totals
| Turbine 1A | Turbine 2A | Turbine 2B | Turbine 3 | Cooling Tower CT-1 | Diesel Starter Engine (1A-DS) | Diesel Fire Pump (FP1)
NOx | 45.8586 | 51.684 | 51.684 | 51.684 | NA | 3.7485 | 2.3153 | 206.9743 | 336.7 | Note: 2019 PTE (51.7x3 + 175 + 4.4 + 2.21)=336.7 ; (51.7x3 + 175)=330.1
VOC | 2.0192 | 12 | 12 | 12 | NA | 0.2975 | 0.18375 | 38.5004 | 43.1 | Note: 2019 PTE (12x3+6.54+0.4+0.18)=43.12; (12x3+6.54)=42.54
Lead | 0.0009198 | NA | NA | NA | NA | NA | NA | 0.0009198
CO | 7.7745 | 175.2 | 175.2 | 175.2 | NA | 0.8075 | 0.49875 | 534.6807 | 582.4
PM10 | 0.3285 | 29.346 | 29.346 | 29.346 | 9.7577 | 0.238 | 0.147 | 98.5092 | 102.6
PM2.5 | 0.3285 | 29.346 | 29.346 | 29.346 | 9.7577 | 0.238 | 0.147 | 98.5092 | 102.6
SOx | 13.797 | 11.388 | 11.388 | 11.388 | NA | 0.2465 | 0.15225 | 48.3597 | 133.8
Ammonia | NA | 61.32 | 61.32 | 61.32 | NA | NA | NA | 183.96 | 183.9
Total HAP (incl. CH2O) | 0.1042 | 4.0739 | 4.0739 | 4.0739 | NA | 0.0054856 | 0.0033881 | 12.3348
[11 empty] | RACT III Total NOx Reduction | RACT III CT NOx Reduction
[11 empty] | 336.7 | 330.1
[11 empty] | 194.8468 | 200.9106
[11 empty] | 141.8531 | 129.1894
Note on C27: Lipari, Bernadette: 175 tpy for R2
Note on O27: Lipari, Bernadette: This is a R2 reduction. Prior to R2, NOx=1,152 tpy.
Note on C28: Lipari, Bernadette: 6.54 tpy for R2
Note on O28: Lipari, Bernadette: This is a R2 reduction. Prior to R2, VOC=80.2 tpy.

## Brunot Island CT PTE
|  |  | Company Name: | Brunot Island Generating Station
|  |  | Address: | Brunot Island, Pittsburhg, PA
|  |  | Title V Operating Permit: | 0056-OP25
|  |  | Reviewer: | BL
|  |  | Date: | 2024-08-13
1. Process Description
Unit | Unit Description |  | Fuel | Gross Max.Electric Power (MW) | Total Heat Input Capacity (MMBtu/hr) | Max. Potential Throughput (MMCF/yr) | Btu/Gal | Btu/CF | Max. hrs/yr | Steady-State hrs/yr | Annual Capacity Factor |  | Note: per 6-30-2000 application; each unit is 898 MMBtu/hr and 1020 BTU/scf
Note: Per IP1a, the HRSG = 240 MMBtu/hr
Note: BACT standard or PM since IP1 has been 0.015 lb/MMbtu for PM
Turbine 1A | Simple Cylce |  | # 2 Fuel Oil | 22 | 300 | NA | 138211 | NA | 438 | 438 | 5%
Turbine 2A | Combined Cycle Power Block (a) |  | Natural Gas | 63 | 918 | 7747.2832 | NA | 1038 | 8760 | 8760 | NA
Turbine 2B | Combined Cycle Power Block (a) |  | Natural Gas | 63 | 918 | 7747.2832 | NA | 1038 | 8760 | 8760 | NA
Turbine 3 | Combined Cycle Power Block (a) |  | Natural Gas | 63 | 918 | 7747.2832 | NA | 1038 | 8760 | 8760 | NA
2. Emission Factors
Unit 1A
Emission Factors (lb/MMBTU)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb (b) | Formaldehyde
0.005 | 0.005 | 0.005 | 0.698 | 0.030733 | 0.11833 | 0.21 | NA | NA | NA | 1.4e-05 | 0.00028
Units 2A, 2B & 3
Emission Facotrs (lb/MMBTU)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb (b) | Formaldehyde
0.015 | 0.015 | 0.015 | 0.012854 | 0.0029845 | 0.043573 | 0.00286 | NA | 0.015251 | NA | NA | 0.00071
3. Combustion Emissions - Criteria Pollutants
Unit 1A
Potential to Emit (lbs/hr) (a)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb (b) | Formaldehyde
1.5 | 1.5 | 1.5 | 209.4 | 9.22 | 35.5 | 63 | NA | NA | NA | 0.0042 | 0.084018
[11 empty] | 0.0184 | tpy
Potential to Emit (lbs/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
657 | 657 | 657 | 91717.2 | 4038.36 | 15549 | 27594 | NA | NA | NA | 1.8396 | 36.8
Potential to Emit (tons/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
0.3285 | 0.3285 | 0.3285 | 45.8586 | 2.0192 | 7.7745 | 13.797 | NA | NA | NA | 0.0009198 | 0.0184
(a) Permit No. OP#1065006-000-23600/RACT | [10 empty] | 0.018396
Unit 2A
Potential to Emit (lbs/hr) (a)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb (b) | Formaldehyde
6.7 | 6.7 | 6.7 | 11.8 | 3 | 40 | 2.6 | NA | 14 | NA | NA | 0.64
Potential to Emit (lbs/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
58692 | 58692 | 58692 | 103368 | 26280 | 350400 | 22776 | NA | 122640 | NA | NA | 5606.4
Potential to Emit (tons/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
29.346 | 29.346 | 29.346 | 51.684 | 12 | 175.2 | 11.388 | NA | 61.32 | NA | NA | 2.8032
(a) Manufacturer's Spec/BACT - Permit No. 0056-I001a
Unit 2B
Potential to Emit (lbs/hr) (a)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb (b) | Formaldehyde
6.7 | 6.7 | 6.7 | 11.8 | 3 | 40 | 2.6 | NA | 14 | NA | NA | 0.64
Potential to Emit (lbs/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
58692 | 58692 | 58692 | 103368 | 26280 | 350400 | 22776 | NA | 122640 | NA | NA | 5606.4
Potential to Emit (tons/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
29.346 | 29.346 | 29.346 | 51.684 | 12 | 175.2 | 11.388 | NA | 61.32 | NA | NA | 2.8032
(a) Manufacturer's Spec/BACT - Permit No. 0056-I001
Unit 3
Potential to Emit (lbs/hr) (a)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb (b) | Formaldehyde
6.7 | 6.7 | 6.7 | 11.8 | 3 | 40 | 2.6 | NA | 14 | NA | NA | 0.64
Potential to Emit (lbs/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
58692 | 58692 | 58692 | 103368 | 26280 | 350400 | 22776 | NA | 122640 | NA | NA | 5606.4
[8 empty] | - | -
Potential to Emit (tons/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
29.346 | 29.346 | 29.346 | 51.684 | 12 | 175.2 | 11.388 | NA | 61.32 | NA | NA | 2.8032
(a) Manufacturer's Spec/BACT - Permit No. 0056-I001
4. Combustion Emissions - Total
Total Potential to Emit (tons/yr)
PM | PM10 | PM2.5 | NOX | VOC | CO | SO2 | CO2 | NH3 | H2SO4 | Pb | Formaldehyde
88.3665 | 88.3665 | 88.3665 | 200.9106 | 38.0192 | 533.3745 | 47.961 | NA | 183.96 | NA | 0.0009198 | 8.428
5. Combustion Emissions - HAPs
Unit 1A
[5 empty] | Potential Emissions (Annual Emissions Based on 5% Capacity Factor) |  | Permit Limits (TVOP Table V-B-1 & RACT Installation Permit 056-I002)
[5 empty] | lbs/hr | tons/yr | lbs/hr | tons/yr
Total HAPs |  |  |  |  | 0.47579 | 0.1042 | NA | NA
1,3 Butadiene | 1.6e-05 | lb/MMBTU | AP-42 3.1-4 |  | 0.0048 | 0.0010512 | NA | NA
Benzene | 5.5e-05 | lb/MMBTU | AP-42 3.1-4 |  | 0.0165 | 0.0036135 | NA | NA
Formaldehyde | 0.00028 | lb/MMBTU | AP-42 3.1-4 |  | 0.084 | 0.018396 | NA | NA
Naphthalene | 3.5e-05 | lb/MMBTU | AP-42 3.1-4 |  | 0.0105 | 0.0022995 | NA | NA
PAHs | 5e-06 | lb/MMBTU | AP-42 3.1-4 |  | 0.0015 | 0.0003285 | NA | NA
Hydrochloric Acid | 0.046 | lb/1000 gal | Fuel Test Data 1 | 1/14/2010 Test Data | 0.099912 | 0.021881 | NA | NA
Arsenic | 1.1e-05 | lb/MMBTU | AP-42 3.1-5 |  | 0.0033 | 0.0007227 | NA | NA
Beryllium | 3.1e-07 | lb/MMBTU | AP-42 3.1-5 |  | 9.3e-05 | 2.0367e-05 | NA | NA
Cadmium | 4.8e-06 | lb/MMBTU | AP-42 3.1-5 |  | 0.00144 | 0.00031536 | NA | NA
Chromium | 1.1e-05 | lb/MMBTU | AP-42 3.1-5 |  | 0.0033 | 0.0007227 | NA | NA
Lead | 1.4e-05 | lb/MMBTU | AP-42 3.1-5 |  | 0.0042 | 0.0009198 | NA | NA
Manganese | 0.00079 | lb/MMBTU | AP-42 3.1-5 |  | 0.237 | 0.051903 | NA | NA
Mercury | 1.2e-06 | lb/MMBTU | AP-42 3.1-5 |  | 0.00036 | 7.884e-05 | NA | NA
Nickel | 4.6e-06 | lb/MMBTU | AP-42 3.1-5 |  | 0.00138 | 0.00030222 | NA | NA
Selenium | 2.5e-05 | lb/MMBTU | AP-42 3.1-5 |  | 0.0075 | 0.0016425 | NA | NA
1 Calculation: E.F. x 2172 gal/hr / 1000; (300 MMBtu/hr x 1000000 / 138000 Btu/gal = 2172 gal/hr; 138000 Btu/gal is the Gross Caloric Value of #2 Fuel Oil (BTU/gal from 2024 E.I.)
Units 2A, 2B, & 3
[5 empty] | Unit 2A: Potential Emissions |  | Unit 2A: Potential Emissions |  | Unit 3: Potential Emissions |  | Permit Limits (TVOP Table V-B-1)
[5 empty] | lbs/hr | tons/yr | lbs/hr | tons/yr | lbs/hr | tons/yr | lbs/hr/unit | tons/yr/unit
Total HAPs |  |  |  |  | 0.93012 | 4.0739 | 0.93012 | 4.0739 | 0.93012 | 4.0739 | NA | NA
1,3 Butadiene | 4.3e-07 | lb/MMBTU | AP-42 3.1-3 |  | 0.00039474 | 0.001729 | 0.00039474 | 0.001729 | 0.00039474 | 0.001729 | NA | NA
Acetaldehyde | 4e-05 | lb/MMBTU | AP-42 3.1-3 |  | 0.03672 | 0.16083 | 0.03672 | 0.16083 | 0.03672 | 0.16083 | NA | NA
Acrolein | 6.4e-06 | lb/MMBTU | AP-42 3.1-3 |  | 0.0058752 | 0.025733 | 0.0058752 | 0.025733 | 0.0058752 | 0.025733 | NA | NA
Benzene | 1.2e-05 | lb/MMBTU | AP-42 3.1-3 |  | 0.011016 | 0.04825 | 0.011016 | 0.04825 | 0.011016 | 0.04825 | NA | NA
Ethyl benzene | 3.2e-05 | lb/MMBTU | AP-42 3.1-3 |  | 0.029376 | 0.12867 | 0.029376 | 0.12867 | 0.029376 | 0.12867 | NA | NA
Formaldehyde | 0.00069717 | lb/MMBTU | TVOP Table V-B-1 | EF = Permit hourly limit/Firing Capacity | 0.64 | 2.8032 | 0.64 | 2.8032 | 0.64 | 2.8032 | 0.64 | 2.8
Naphthalene | 1.3e-06 | lb/MMBTU | AP-42 3.1-3 |  | 0.0011934 | 0.0052271 | 0.0011934 | 0.0052271 | 0.0011934 | 0.0052271 | NA | NA
PAHs | 9e-07 | lb/MMBTU | AP-42 3.1-3 |  | 0.0008262 | 0.0036188 | 0.0008262 | 0.0036188 | 0.0008262 | 0.0036188 | NA | NA
Propylene oxide | 2.9e-05 | lb/MMBTU | AP-42 3.1-3 |  | 0.026622 | 0.1166 | 0.026622 | 0.1166 | 0.026622 | 0.1166 | NA | NA
Toluene | 0.00013 | lb/MMBTU | AP-42 3.1-3 |  | 0.11934 | 0.52271 | 0.11934 | 0.52271 | 0.11934 | 0.52271 | NA | NA
Xylenes | 6.4e-05 | lb/MMBTU | AP-42 3.1-3 |  | 0.058752 | 0.25733 | 0.058752 | 0.25733 | 0.058752 | 0.25733 | NA | NA
Note on I12: Lipari, Bernadette: 2000 IP application: this is 138477 btu/gal on pdf p. 50 Max 2166 gal/hr
Note on K12: Lipari, Bernadette: App states that this is 8760. Adjusted to 438 based on 5% capacity factor.
Note on H13: Lipari, Bernadette: 2024 app: actual is 267,418 MCF pdf p. 40
Note on H14: Lipari, Bernadette: 2024 app: actual is 219,129 MCF/yr pdf p. 48
Note on H15: Lipari, Bernadette: 2024 app: actual is 123,788 MCF/yr pdf p. 56
Note on B45: Lipari, Bernadette: App states that the lb/hr limits aren't applicable during startup and shutdown pdf p. 45
Note on M120: Lipari, Bernadette: All limits from IP1 are Mfg Specs/BACT for criteria pollutants

## Cooling Tower
|  |  |  | Company Name: | Brunot Island Generating Station
|  |  |  | Address: | Brunot Island, Pittsburhg, PA
|  |  |  | Title V Operating Permit: | 0056-OP25
|  |  |  | Reviewer: | BL
|  |  |  | Date: | 2024-08-13
Cooling Tower:
Circulating Water Design Rate: | 84000 | GPM
Design Drift Rate: | 0.005 | %
TDS of circulating water: | 1060 | ppmw
Hours of Cooling Tower Operation: | 8760 | hours
Weight of gallon of water | 8.34 | lbs/gal (AP-42)
Cooling Tower particulate emissions
Cooling Tower - Unit 1
Description | Value | Units | Reference
Circulating water rate (design) | 84000 | gpm | Operating Manual for the Circulating Water System, Marley Cooling Tower Model No. 6516-4-04
Weight of water | 8.34 | lbs/gal | Constant (AP-42)
Circulating water | 42033600 | lbs/hr
Drift rate (design) | 0.005 | % | Fax Dated 11/29/2000 from Marley Cooling Tower Company
Water released to atmosphere via droplets | 2101.68 | lbs/hr
Total dissolved solids | 1060 | ppm | Based on calculations from Brunot Island NPDES Permit Renewal Application, November 1999
Conservative estimate of total emissions | 2.2278 | lbs/hr
hours per year (TYP) | 8760 | hrs | Potential Operating Hours
PM10 Emissions | 9.7577 | (tons/year)
PM2.5 Emissions | 9.7577 | tons/yr

## Generator
[6 empty] | Company Name: | Brunot Island Generating Station
[6 empty] | Address: | Brunot Island, Pittsburhg, PA
[6 empty] | Title V Operating Permit: | 0056-OP25
[6 empty] | Reviewer: | BL
[6 empty] | Date: | 2024-08-26
Starting Diesel (DS001)
|  |  | Emission Factor (lb/MMBtu) | [9 empty] | Fuel Oil Sulfur Content (%)
Engine Type |  |  | PM | PM10 | SO2 3 | SO2 (0.0081S) 4 | NOX | VOC | CO | HAPs |  |  | 0.0015
Diesel-fired Engines 1a |  |  | 0.31 | 0.31 | 0.29 | 1.215e-05 | 4.41 | 0.35 | 0.95 |  |  |  | Fuel Oil Heat Content (MMBtu/kgal)
Article XXI, §2104.02.a.1 2 (lb/MMBtu) |  |  | 0.28 | 0.28 | [8 empty] | 140
1a Emission factors for diesel engines are from AP 42, Chapter 3.3, Tables 3.3-1. (10/96)
2 Pursuant to §2104.02.a.1, particulate emissions from combustion units with heat input greater than 0.5 MMBtu per hour shall not exceed 0.28 lb/MMBtu of actual heat input at any time while combusting grade no. 2 fuel oil.
3 AP-42, Table 3.3-1; Diesel Engines <600hp.
4 AP-42, Table 3.4-1; Diesel Engines >600hp. Diesel fuel sulfur content = 0.0015% (15 ppm) | Emission Factor (lb/hp-hr) | [6 empty] | Emission Factor (lb/MMBtu) |  |  |  | Fuel Oil Sulfur Content (%)
Engine Type | PM | PM10 | SO2 (0.0081S) | NOx | VOC |  | CO | HAPs |  |  |  | 0.0015
Diesel-fired Engines > 600 hp 1a | 0.0007 | 0.0007 | 1.2135e-05 | 0.024 | 0.0007 |  | 0.0055 | 0.001492 |  |  |  | Fuel Oil Heat Content (MMBtu/kgal)
Diesel-fired Engines < 600 hp 1b | 0.0022 | 0.0022 | 0.00205 | 0.031 | 0.00251 |  | 0.00668 | 0.00379 |  |  |  | 140
Article XXI, §2104.02.a.1 2 (lb/MMBtu) | 0.28 | 0.28
1a Emission factors for diesel engines are from AP 42, Chapter 3.4, Tables 3.4-1, 3.4-2, 3.4-3 and 3.4-4. (10/96)
1b Emission factors for diesel engines are from AP 42, Chapter 3.3, Tables 3.3-1 and 3.3-2. (10/96)
2 Pursuant to §2104.02.a.1, particulate emissions from combustion units with heat input greater than 0.5 MMBtu per hour shall not exceed 0.28 lb/MMBtu of actual heat input at any time while combusting grade no. 2 fuel oil.
4 AP-42, Table 3.4-1; Diesel Engines >600hp. Diesel fuel sulfur content = 0.0015% (15 ppm)
[5 empty] | Potential to Emit (lbs/hr) | [6 empty] | Potential to Emit (tons/yr)
Power Output (KW) | Power Output (hp) | Maximum Heat Input Capacity (MMBtu/hr) | Annual Fuel Consumption (gal) | Hours of Operation (hr/yr) | PM | PM10 | SO2 | NOx | VOC | CO | HAPs | PM | PM10 | SO2 | NOx | VOC | CO | HAPs
| 460 | 3.4 |  | 500 | 0.952 | 0.952 | 0.986 | 14.994 | 1.19 | 3.23 | 0.021942 | 0.238 | 0.238 | 0.2465 | 3.7485 | 0.2975 | 0.8075 | 0.0054856
Potential Emissions
[5 empty] | lbs/hr | tons/yr
Total HAPs |  |  |  |  | 0.021942 | 0.0054856
Benzene | 0.000933 | lb/MMBTU | AP-42 3.3-2 |  | 0.0031722 | 0.00079305
Toluene | 0.000409 | lb/MMBTU | AP-42 3.3-2 |  | 0.0013906 | 0.00034765
Xylenes | 0.000285 | lb/MMBTU | AP-42 3.3-2 |  | 0.000969 | 0.00024225
Propylene | 0.00258 | lb/MMBTU | AP-42 3.3-2 |  | 0.008772 | 0.002193
1,3 Butadiene | 3.91e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.00013294 | 3.3235e-05
Formaldehyde | 0.00118 | lb/MMBTU | AP-42 3.3-2 |  | 0.004012 | 0.001003
Acetaldehyde | 0.000767 | lb/MMBTU | AP-42 3.3-2 |  | 0.0026078 | 0.00065195
Acrolein | 9.25e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.0003145 | 7.8625e-05
Naphthalene | 8.48e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.00028832 | 7.208e-05
PAHs | 8.32e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.00028288 | 7.072e-05
Note on D30: Lipari, Bernadette: exempt based on PADEP 127.14(a)3 less than 10 MMBtu/hr

## Fire Pump
[7 empty] | Company Name: | Brunot Island Generating Station
[7 empty] | Address: | Brunot Island, Pittsburhg, PA
[7 empty] | Title V Operating Permit: | 0056-OP25
[7 empty] | Reviewer: | BL
[7 empty] | Date: | 2024-08-26
Fire Pump (FP0001)
|  |  |  | Emission Factor (lb/MMBtu) | [9 empty] | Fuel Oil Sulfur Content (%)
| Engine Type |  |  | PM | PM10 | SO2 3 | SO2 (0.0081S) 4 | NOX | VOC | CO | HAPs |  |  | 0.0015
| Diesel-fired Engines 1a |  |  | 0.31 | 0.31 | 0.29 | 1.215e-05 | 4.41 | 0.35 | 0.95 |  |  |  | Fuel Oil Heat Content (MMBtu/kgal)
| Article XXI, §2104.02.a.1 2 (lb/MMBtu) |  |  | 0.28 | 0.28 | [8 empty] | 140
1a Emission factors for diesel engines are from AP 42, Chapter 3.3, Tables 3.3-1. (10/96)
2 Pursuant to §2104.02.a.1, particulate emissions from combustion units with heat input greater than 0.5 MMBtu per hour shall not exceed 0.28 lb/MMBtu of actual heat input at any time while combusting grade no. 2 fuel oil.
3 AP-42, Table 3.3-1; Diesel Engines <600hp.
4 AP-42, Table 3.4-1; Diesel Engines >600hp. Diesel fuel sulfur content = 0.0015% (15 ppm)
|  | Emission Factor (lb/hp-hr) | [6 empty] | Emission Factor (lb/MMBtu) |  |  |  | Fuel Oil Sulfur Content (%)
Engine Type |  | PM | PM10 | SO2 (0.0081S) | NOx | VOC |  | CO | HAPs |  |  |  | 0.0015
Diesel-fired Engines > 600 hp 1a |  | 0.0007 | 0.0007 | 1.2135e-05 | 0.024 | 0.0007 |  | 0.0055 | 0.001492 |  |  |  | Fuel Oil Heat Content (MMBtu/kgal)
Diesel-fired Engines < 600 hp 1b |  | 0.0022 | 0.0022 | 0.00205 | 0.031 | 0.00251 |  | 0.00668 | 0.00379 |  |  |  | 140
Article XXI, §2104.02.a.1 2 (lb/MMBtu) |  | 0.28 | 0.28
1a Emission factors for diesel engines are from AP 42, Chapter 3.4, Tables 3.4-1, 3.4-2, 3.4-3 and 3.4-4. (10/96)
1b Emission factors for diesel engines are from AP 42, Chapter 3.3, Tables 3.3-1 and 3.3-2. (10/96)
2 Pursuant to §2104.02.a.1, particulate emissions from combustion units with heat input greater than 0.5 MMBtu per hour shall not exceed 0.28 lb/MMBtu of actual heat input at any time while combusting grade no. 2 fuel oil.
[6 empty] | Potential to Emit (lbs/hr) | [6 empty] | Potential to Emit (tons/yr)
| Power Output (KW) | Power Output (hp) | Maximum Heat Input Capacity (MMBtu/hr) | Annual Fuel Consumption (gal) | Hours of Operation (hr/yr) | PM | PM10 | SO2 | NOx | VOC | CO | HAPs | PM | PM10 | SO2 | NOx | VOC | CO | HAPs
|  | 285 | 2.1 |  | 500 | 0.588 | 0.588 | 0.609 | 9.261 | 0.735 | 1.995 | 0.013553 | 0.147 | 0.147 | 0.15225 | 2.3153 | 0.18375 | 0.49875 | 0.0033881
Potential Emissions
[6 empty] | lbs/hr | tons/yr
| Total HAPs |  |  |  |  | 0.013553 | 0.0033881
| Benzene | 0.000933 | lb/MMBTU | AP-42 3.3-2 |  | 0.0019593 | 0.00048983
| Toluene | 0.000409 | lb/MMBTU | AP-42 3.3-2 |  | 0.0008589 | 0.00021473
| Xylenes | 0.000285 | lb/MMBTU | AP-42 3.3-2 |  | 0.0005985 | 0.00014962
| Propylene | 0.00258 | lb/MMBTU | AP-42 3.3-2 |  | 0.005418 | 0.0013545
| 1,3 Butadiene | 3.91e-05 | lb/MMBTU | AP-42 3.3-2 |  | 8.211e-05 | 2.0528e-05
| Formaldehyde | 0.00118 | lb/MMBTU | AP-42 3.3-2 |  | 0.002478 | 0.0006195
| Acetaldehyde | 0.000767 | lb/MMBTU | AP-42 3.3-2 |  | 0.0016107 | 0.00040268
| Acrolein | 9.25e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.00019425 | 4.8563e-05
| Naphthalene | 8.48e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.00017808 | 4.452e-05
| PAHs | 8.32e-05 | lb/MMBTU | AP-42 3.3-2 |  | 0.00017472 | 4.368e-05
Note on D29: Lipari, Bernadette: exempt based on PADEP 127.14(a)3 less than 10 MMBtu/hr

## Input Data
Sub-Facility: |  | Date Installed: | 1972-02-01 | RATED INPUT (MMBTU/HR): | 300
Name: | Turbine 1A |  |  | Hours: | 438 | Miscellaneous Data
Oil:
[6 empty] | Weight of oil | 7.05 | lb/gal
Fuel: | NA | Fuel Material Location
| # 2 Fuel Oil | Fuel / Material
| 20100101 | SCC Code
| NA | % ASH |  |  |  | Cooling Tower:
| 0.0738 | % SULFUR |  |  |  | Circulating Water Design Rate: | 84000 | GPM
| 138211 | Btu / Gal-Lb-CF |  |  |  | Design Drift Rate: | 0.005 | %
[6 empty] | TDS of circulating water: | 1060 | ppmw
| Gallons |  | Hours |  |  | Hours of Cooling Tower Operation: | 8760 | hours
Fuel Use: | 80746.1056 | JAN | 36.5 |  |  | Weight of gallon of water | 8.34 | lbs/gal (AP-42)
| 72931.9663 | FEB | 36.5
| 80746.1056 | MAR | 36.5 |  |  | Cooling Tower particulate emissions
| 78141.3925 | APR | 36.5
| 80746.1056 | MAY | 36.5 |  |  | Cooling Tower - Unit 1
| 78141.3925 | JUN | 36.5
| 80746.1056 | JUL | 36.5 |  |  | Description | Value | Units | Reference
| 80746.1056 | AUG | 36.5 |  |  | Circulating water rate (design) | 84000 | gpm | Operating Manual for the Circulating Water System, Marley Cooling Tower Model No. 6516-4-04
| 78141.3925 | SEP | 36.5 |  |  | Weight of water | 8.34 | lbs/gal | Constant (AP-42)
| 80746.1056 | OCT | 36.5 |  |  | Circulating water | 42033600 | lbs/hr
| 78141.3925 | NOV | 36.5 |  |  | Drift rate (design) | 0.005 | % | Fax Dated 11/29/2000 from Marley Cooling Tower Company
| 80746.1056 | DEC | 36.5 |  |  | Water released to atmosphere via droplets | 2101.68 | lbs/hr
Total: | 950720.2755 | Gal / Tons / MCF | 438 |  |  | Total dissolved solids | 1060 | ppm | Based on calculations from Brunot Island NPDES Permit Renewal Application, November 1999
[6 empty] | Conservative estimate of total emissions | 2.2278 | lbs/hr
[6 empty] | hours per year (TYP) | 8760 | hrs | Potential Operating Hours
Operating | 7 | Days Per Week
Time: | 365 | Total Days |  |  |  | PM10 Emissions | 9.7577 | (tons/year)
| 438 | Total Hours |  |  |  | PM2.5 Emissions | 9.7577 | tons/yr
Sub-Facility: |  | Date Installed: | 1973-1974 | RATED INPUT (MMBTU/HR): | 918
Name: | Turbine 2A |  |  | Hours: | 8760
Fuel: | NA | Fuel Material Location
| Natural Gas | Fuel / Material
| 20100201 | SCC Code
| N/A | % ASH
| N/A | % SULFUR
| 1038 | Btu / Gal-Lb-CF
MCF
Fuel Use: | 172023.1214 | JAN | 172023.1214
| 155375.7225 | FEB
| 172023.1214 | MAR
| 166473.9884 | APR
| 172023.1214 | MAY
| 166473.9884 | JUN
| 172023.1214 | JUL
| 172023.1214 | AUG
| 166473.9884 | SEP
| 172023.1214 | OCT
| 166473.9884 | NOV
| 172023.1214 | DEC
Total: | 2025433.526 | Gal / Tons / MCF
Operating | 7 | Days Per Week
Time: | 365 | Total Days
| 8760 | Total Hours
Sub-Facility: |  | Date Installed: | 1973-1974 | RATED INPUT (MMBTU/HR): | 918
Name: | Turbine 2B |  |  | Hours: | 8760
Fuel: | NA | Fuel Material Location
| Natural Gas | Fuel / Material
| 20100201 | SCC Code
| N/A | % ASH
| N/A | % SULFUR
| 1038 | Btu / Gal-Lb-CF
MCF
Fuel Use: | 172023.1214 | JAN
| 155375.7225 | FEB
| 172023.1214 | MAR
| 166473.9884 | APR
| 172023.1214 | MAY
| 166473.9884 | JUN
| 172023.1214 | JUL
| 172023.1214 | AUG
| 166473.9884 | SEP
| 172023.1214 | OCT
| 166473.9884 | NOV
| 172023.1214 | DEC
Total: | 2025433.526 | Gal / Tons / MCF
Operating | 7 | Days Per Week
Time: | 365 | Total Days
| 8760 | Total Hours
Sub-Facility: |  | Date Installed: | 1973-1974 | RATED INPUT (MMBTU/HR): | 918
Name: | Turbine 3 |  |  | Hours: | 8760
Fuel: | NA | Fuel Material Location
| Natural Gas | Fuel / Material
| 20100201 | SCC Code
| N/A | % ASH
| N/A | % SULFUR
| 1038 | Btu / Gal-Lb-CF
MCF
Fuel Use: | 172023.1214 | JAN
| 155375.7225 | FEB
| 172023.1214 | MAR
| 166473.9884 | APR
| 172023.1214 | MAY
| 166473.9884 | JUN
| 172023.1214 | JUL
| 172023.1214 | AUG
| 166473.9884 | SEP
| 172023.1214 | OCT
| 166473.9884 | NOV
| 172023.1214 | DEC
Total: | 2025433.526 | Gal / Tons / MCF
Operating | 7 | Days Per Week
Time: | 365 | Total Days
| 8760 | Total Hours
Sub-Facility: | DS001 | Date Installed: | 2011-01-01 | RATED INPUT (MMBTU/HR): | 3.4
Name: | Starting Diesel |  |  | HP: | 460
Fuel: | NA | Fuel Material Location
| # 2 Fuel Oil | Fuel / Material
| 20100101 | SCC Code
| NA | % ASH
| 0.0015 | % SULFUR
| 129250 | Btu / Gal-Lb-CF
Gallons
Fuel Use: | 1096.0671 | JAN
| 1096.0671 | FEB
| 1096.0671 | MAR
| 1096.0671 | APR
| 1096.0671 | MAY
| 1096.0671 | JUN
| 1096.0671 | JUL
| 1096.0671 | AUG
| 1096.0671 | SEP
| 1096.0671 | OCT
| 1096.0671 | NOV
| 1096.0671 | DEC
Total: | 13152.8046 | Gal / Tons / MCF
Operating | 7 | Days Per Week
Time: | 365 | Total Days
| 500 | Total Hours
Sub-Facility: | FP0001 | Date Installed: | 2011-01-01 | RATED INPUT (MMBTU/HR): | 2.1
Name: | Fire Pump |  |  | HP: | 285
Fuel: | NA | Fuel Material Location
| # 2 Fuel Oil | Fuel / Material
| 20100101 | SCC Code
| NA | % ASH
| 0.0015 | % SULFUR
| 129250 | Btu / Gal-Lb-CF
Gallons
Fuel Use: | 676.9826 | JAN
| 676.9826 | FEB
| 676.9826 | MAR
| 676.9826 | APR
| 676.9826 | MAY
| 676.9826 | JUN
| 676.9826 | JUL
| 676.9826 | AUG
| 676.9826 | SEP
| 676.9826 | OCT
| 676.9826 | NOV
| 676.9826 | DEC
Total: | 8123.7911 | Gal / Tons / MCF
Operating | 7 | Days Per Week
Time: | 365 | Total Days
| 500 | Total Hours
Note on B27: Lipari, Bernadette: gallons per year

## Emission Factors
UnitType | UnitName | Pollutant | EF | Unit | Reference | EF Used for Calc | EF Used for Calc Unit |  | Input New Default HAPs (112b) and 112r Emission Factors Here | [21 empty] | Greenhouse Gas Emission Factors
Turbines - Oil Fired | Turbine 1A | NH3 | NA |  | No factor available | [25 empty] | 40 CFR 98 Table C-1 and C-2
Turbines - Oil Fired | Turbine 1A | FPM | 0.005 | lb/MMBtu | ACHD TVOP No. 0056 |  |  | 0.005
Turbines - Oil Fired | Turbine 1A | PMCond | 0.0072 | lb/MMBtu | AP-42 Table 3.1-2a | [11 empty] | Boilers | [6 empty] | Combustion Turbines |  |  | Large Diesel Engines |  | Small Diesel Engines |  | Fuel | Emission Factor (kg/MMBtu)
Turbines - Oil Fired | Turbine 1A | FPM-10 | 0.005 | lb/MMBtu | ACHD TVOP No. 0056 |  |  | 0.005 | [18 empty] | (> 600hp) |  | (< 600hp) |  |  | CO2 | N2O | CH4
Turbines - Oil Fired | Turbine 1A | FPM 2.5 | NA |  | No factor available | [8 empty] | Coal Combustion |  | Oil Combustion |  |  |  | Gas Combustion |  | Oil Combustion |  | Gas Combustion |  |  | Diesel Combustion |  | Diesel Combustion |  | Bituminous Coal | 93.28 | 0.0016 | 0.011
Turbines - Oil Fired | Turbine 1A | SO2 | 0.21 | lb/MMBtu | ACHD TVOP No. 0056a |  |  | 0.21 | [22 empty] | Subbituminous Coal | 97.17 | 0.0016 | 0.011
Turbines - Oil Fired | Turbine 1A | NOx | 0.698 | lb/MMBtu | ACHD Installation Permit No. 0056-I002 |  |  | 0.698 | [7 empty] | No.2, Distillate Oil | [5 empty] | No.2, Distillate Oil |  |  |  | % Pollutant/ |  |  |  |  | Natural Gas | 53.06 | 0.0001 | 0.001
Turbines - Oil Fired | Turbine 1A | VOC | 0.030733 | lb/MMBtu | Calculation using lb/hr limit in IP 0056-I002 and Maximum Design Rate (300 MMBtu/hr) |  |  | 0.030733 | Pollutant | CAS # | 112(b) ? | 112(r) ? | VOC | (lb/ton) | Reference | (lb/MMBtu) | Reference | (lb/1000 gal) | Reference | (lb/10^6 scf) | Reference | (lb/MMBtu) | Reference | (lb/MMBtu) | Reference | Total VOC | (lb/MMBtu) | Reference | (lb/MMBtu) | Reference | Distillate Fuel Oil No. 2 | 73.96 | 0.0006 | 0.003
Turbines - Oil Fired | Turbine 1A | CO | 0.11833 | lb/MMBtu | Calculation using lb/hr limit in TVOP and Maximum Design Rate (300 MMBtu/hr) |  |  | 0.11833 | 1,3 Butadiene | 106-99-0 | yes |  | VOC | 0 |  | 0 |  | 0 |  | 0 |  | 1.6e-05 | 18 | 4.3e-07 | 17 | 0.00043128 | 0 |  | 3.91e-05 | 14 | Distillate Fuel Oil No. 6 | 75.1 | 0.0006 | 0.003
Turbines - Oil Fired | Turbine 1A | CO2 | [6 empty] | 1,1,1-Trichloroethane | 71-55-6 | yes |  | VOC | 2e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | Kerosene | 75.2 | 0.0006 | 0.003
Turbines - Oil Fired | Turbine 1A | OC | [6 empty] | 2,3,7,8 -Tetrachlorodibenzo p dioxin | 1746-01-6 | yes |  | VOC | 1.43e-11 | 15 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | Propane | 62.87 | 0.0006 | 0.003
Turbines - Gas Fired | Turbine 2A | NH3 | 0.015251 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  | 0.015251 | 2,4-Dinitrotoluene | 121-14-2 | yes |  | VOC | 2.8e-07 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2A | FPM | 0.015 | lb/MMBtu | (ACHD TVOP No. 0056) IP1; Article XXI 2104.02.a.1.A |  |  | Article XXI 2104.02.a.1.A | 2-Chloroacetophenone | 532-27-4 | yes |  | VOC | 7e-06 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | Global Warming Potentials
Turbines - Gas Fired | Turbine 2A | PMCond | 0.0047 | lb/MMBtu | AP-42 Table 3.1-2a |  |  |  | Acetaldehyde | 75-07-0 | yes |  | VOC | 0.00057 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 4e-05 | 17 | 0.040119 | 2.52e-05 | 12 | 0.000767 | 14 | GHG | CAS No | GWP
Turbines - Gas Fired | Turbine 2A | FPM-10 | 0.015 | lb/MMBtu | ACHD TVOP No. 0056 |  |  | Article XXI 2104.02.a.1.A | Acetophenone | 98-86-2 | yes |  | VOC | 1.5e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | CO2 | 124-38-9 | 1
Turbines - Gas Fired | Turbine 2A | FPM 2.5 | NA |  | No factor available |  |  |  | Acrolein | 107-02-8 | yes |  | VOC | 0.00029 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 6.4e-06 | 17 | 0.0064191 | 7.88e-06 | 12 | 9.25e-05 | 14 | N2O | 10024-97-2 | 298
Turbines - Gas Fired | Turbine 2A | SO2 | 0.00286 | lb/MMBtu | ACHD TVOP No. 0056 |  |  | 0.0028322 | Antimony | 7440-36-0 | yes |  |  | 1.8e-05 | 3 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | CH4 | 74-82-8 | 25
Turbines - Gas Fired | Turbine 2A | NOx | 0.012854 | lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  | 0.012854 | Arsenic | 7440-38-2 | yes |  |  | 0.00041 | 3 | 4e-06 | 6 | 0 |  | 0.0002 | 11 | 1.1e-05 | 19 | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2A | VOC | 0.0029845 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  | 0.003268 | Benzene | 1746-01-6 | yes |  | VOC | 0.0013 | 2 | 0 |  | 0 |  | 0.0021 | 10 | 5.5e-05 | 18 | 1.2e-05 | 17 | 0.012036 | 0.000776 | 12 | 0.000933 | 14
Turbines - Gas Fired | Turbine 2A | CO | 0.043573 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  | 0.043573 | Benzyl chloride | 100-44-7 | yes |  | VOC | 0.0007 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | Conversions
Turbines - Gas Fired | Turbine 2A | CO2 | [6 empty] | Beryllium | 7440-41-7 | yes |  |  | 2.1e-05 | 3 | 3e-06 | 6 | 0 |  | 1.2e-05 | 11 | 3.1e-07 | 19 | 0 |  | 0 | 0 |  | 0 |  | 1 kg = | 2.2046 | lbs
Turbines - Gas Fired | Turbine 2A | OC | [6 empty] | Biphenyl | 92-52-4 | yes |  | VOC | 1.7e-06 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 1 mTon = | 1.1023 | ton
Turbines - Gas Fired | Turbine 2B | NH3 | 0.015251 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Bis(2-ethylhexyl)phthalate (DEHP) | 117-81-7 | yes |  | VOC | 7.3e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | FPM | 0.015 | lb/MMBtu | (ACHD TVOP No. 0056) IP1; Article XXI 2104.02.a.1.A |  |  |  | Bromoform | 75-25-2 | yes |  | VOC | 3.9e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | PMCond | 0.0047 | lb/MMBtu | AP-42 Table 3.1-2a |  |  |  | Cadmium | 7440-43-9 | yes |  |  | 5.1e-05 | 3 | 3e-06 | 6 | 0 |  | 0.0011 | 11 | 4.8e-06 | 19 | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | FPM-10 | 0.015 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Carbon disulfide | 75-15-0 | yes |  | VOC | 0.00013 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | FPM 2.5 | NA |  | No factor available |  |  |  | Chlorobenzene | 108-90-7 | yes |  | VOC | 2.2e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | SO2 | 0.00286 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Chloroform | 67-66-3 | yes |  | VOC | 5.9e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | NOx | 0.012854 | lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Chromium | 7440-43-7 | yes |  |  | 0.00026 | 3 | 3e-06 | 6 | 0 |  | 0.0014 | 11 | 1.1e-05 | 19 | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | VOC | 0.0029845 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Cobalt | 7440-48-4 | yes |  |  | 0.0001 | 3 | 0 |  | 0 |  | 8.4e-05 | 11 | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | CO | 0.043573 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Cumene | 98-82-8 | yes |  | VOC | 5.3e-06 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | CO2 | [6 empty] | Cyanide | 57-12-5 | yes |  |  | 0.0025 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 2B | OC | [6 empty] | Dichlorobenzene | 25321-22-6 | yes |  | VOC | 0 |  | 0 |  | 0 |  | 0.0012 | 10 | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | NH3 | 0.015251 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Dimethyl sulfate | 77-78-1 | yes |  | VOC | 4.8e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | FPM | 0.015 | lb/MMBtu | (ACHD TVOP No. 0056) IP1; Article XXI 2104.02.a.1.A |  |  |  | Dioxins (PCDD) |  |  |  | VOC | 6.66e-10 | 15 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | PMCond | 0.0047 | lb/MMBtu | AP-42 Table 3.1-2a |  |  |  | Ethyl benzene | 100-41-4 | yes |  | VOC | 9.4e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 3.2e-05 | 17 | 0.032095 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | FPM-10 | 0.015 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Ethyl chloride | 75-00-3 | yes |  | VOC | 4.2e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | FPM 2.5 | NA |  | No factor available |  |  |  | Ethylene dibromide | 106-93-4 | yes |  | VOC | 1.2e-06 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | SO2 | 0.00286 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Ethylene dichloride | 107-06-2 | yes |  | VOC | 4e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | NOx | 0.012854 | lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Ethylene glycol | 107-21-1 | yes |  |  | plant specific | 16 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | VOC | 0.0029845 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Formaldehyde | 50-00-0 | yes |  | VOC | 0.00024 | 2 | 0 |  | 0.061 | 7 | 0.075 | 10 | 0.00028 | 18 | 0.00071 | 17 | 0.71211 | 7.89e-05 | 12 | 0.00118 | 14
Turbines - Gas Fired | Turbine 3 | CO | 0.043573 | No units lb/MMBtu | Calculation using lb/hr limit in TVOP and maximum annual operating hours (8760) |  |  |  | Furans (PCDF) | 132-64-9 |  |  | VOC | 1.09e-09 | 15 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | CO2 | [6 empty] | Hexane | 110-54-3 | yes |  | VOC | 6.7e-05 | 2 | 0 |  | 0 |  | 1.8 | 10 | 0 |  | 0 |  | 0 | 0 |  | 0
Turbines - Gas Fired | Turbine 3 | OC | [6 empty] | Hydrochloric acid | 7647-01-0 | yes |  |  | plant specific | 5 | 0 |  | 0.046 | 23 | 0 |  | 0.046 | 23 | 0 | 23 | 0 | 0.046 | 23 | 0.046 | 23
Small Oil-Fired Diesel Engines | Starting Diesel | NH3 | NA |  | No factor available |  |  |  | Hydrochloric acid (<0.05% S) | 7647-01-0 | yes |  |  | plant specific | 5 | 0 |  | 0.0036 | 23 | 0 |  | 0.0036 | 23 | 0 | 23 | 0 | 0.0036 | 23 | 0.0036 | 23
Small Oil-Fired Diesel Engines | Starting Diesel | FPM | 0.28 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Hydrofluoric acid | 7664-39-3 | yes |  |  | plant specific | 5 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | PMCond | [6 empty] | Isophorone | 78-59-1 | yes |  | VOC | 0.00058 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | FPM-10 | 0.28 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Lead | 7439-92-1 | yes |  |  | 0.00042 | 3 | 9e-06 | 6 | 0 |  | 0.0005 | 9 | 1.4e-05 | 19 | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | FPM 2.5 | NA |  | No factor available |  |  |  | Manganese | 7439-96-5 | yes |  |  | 0.00049 | 3 | 6e-06 | 6 | 0 |  | 0.00038 | 11 | 0.00079 | 19 | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | SO2 | 2 |  | Calculation using % sulfur and fuel heat content | 0.0016364 | lb/MMBtu |  | Mercury | 7439-97-6 | yes |  |  | plant specific | 5 | 3e-06 | 6 | 0 |  | 0.00026 | 11 | 1.2e-06 | 19 | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | NOx | 4.41 | lb/MMBtu | AP-42 Table 3.3-1 |  |  |  | Methyl bromide | 74-83-9 | yes |  | VOC | 0.00016 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | VOC | 0.36 | lb/MMBtu | AP-42 Table 3.3-1 |  |  |  | Methyl chloride | 74-87-3 | yes |  | VOC | 0.00053 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Starting Diesel | CO | 0.95 | lb/MMBtu | AP-42 Table 3.3-1 |  |  |  | Methyl hydrazine | 60-34-4 | yes |  | VOC | 0.00017 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | NH3 | NA |  | No factor available |  |  |  | Methyl methacrylate | 80-62-6 | yes |  | VOC | 2e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | FPM | 0.28 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Methyl tert butyl ether | 1634-04-4 | yes |  | VOC | 3.5e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | PMCond | [6 empty] | Methylene chloride | 75-09-2 | yes |  | VOC | 0.00029 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | FPM-10 | 0.28 | lb/MMBtu | ACHD TVOP No. 0056 |  |  |  | Naphthalene | 91-20-3 | yes |  | VOC | 1.3e-05 | 1 | 0 |  | 0.000333 | 8 | 0.00061 | 10 | 3.5e-05 | 18 | 1.3e-06 | 17 | 0.0013039 | 0.00013 | 13 | 8.48e-05 | 14
Small Oil-Fired Diesel Engines | Fire Pump | FPM 2.5 | NA |  | No factor available |  |  |  | Nickel | 7440-02-0 | yes |  |  | 0.00028 | 3 | 3e-06 | 6 | 0 |  | 0.0021 | 11 | 4.6e-06 | 19 | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | SO2 | 2 |  | Calculation using % sulfur and fuel heat content | 0.0016364 | lb/MMBtu |  | Phenol | 108-95-2 | yes |  | VOC | 1.6e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | NOx | 4.41 | lb/MMBtu | AP-42 Table 3.3-1 |  |  |  | Polycyclic Organic Matter |  | yes |  | VOC | 6.06e-06 | 1 | 0 |  | 0.0033 | 7 | 8.82e-05 | 10 | 5e-06 | 18 | 9e-07 | 17 | 0.00090268 | 8.2e-05 | 13 | 8.32e-05 | 14
Small Oil-Fired Diesel Engines | Fire Pump | VOC | 0.36 | lb/MMBtu | AP-42 Table 3.3-1 |  |  |  | Propionaldehyde | 123-38-6 | yes |  | VOC | 0.00038 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
Small Oil-Fired Diesel Engines | Fire Pump | CO | 0.95 | lb/MMBtu | AP-42 Table 3.3-1 |  |  |  | Propylene oxide | 76-56-9 | yes | yes |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 2.9e-05 | 17 | 0 | 0 |  | 0
[9 empty] | Selenium | 7782-49-2 | yes |  |  | 0.0013 | 3 | 1.5e-05 | 6 | 0 |  | 2.4e-05 | 11 | 2.5e-05 | 19 | 0 |  | 0 | 0 |  | 0
[9 empty] | Styrene | 100-42-5 | yes |  | VOC | 2.5e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
[9 empty] | Tetrachloroethylene | 127-18-4 | yes |  | VOC | 4.3e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
[9 empty] | Toluene | 108-88-3 | yes |  | VOC | 0.00024 | 2 | 0 |  | 0 |  | 0.0034 | 10 | 0 |  | 0.00013 | 17 | 0.13039 | 0.000281 | 12 | 0.000409 | 14
[9 empty] | Vinyl acetate | 108-05-4 | yes |  | VOC | 7.6e-06 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
[9 empty] | Xylenes | 1330-20-7 | yes |  | VOC | 3.7e-05 | 2 | 0 |  | 0 |  | 0 |  | 0 |  | 6.4e-05 | 17 | 0.064191 | 0.000193 | 12 | 0.000285 | 14
[23 empty] | TOTAL VOC HAP | 0.00099703
[9 empty] | References | [13 empty] | Percent of VOCs that are HAPs (AP-42) | 0.47478
1 - AP-42 Table 1.1-13
2 - AP-42 Table 1.1-14
3 - AP-42 Table 1.1-18
4 - AP-42 Table 1.1-19
5 - ICR Data, 1998
6 - AP-42 Table 1.3-10
7 - AP-42 Table 1.3-8
8 - EPA FIRE 6.23
9 - AP-42 Table 1.4-2
10 - AP-42 Table 1.4-3
11 - AP-42 Table 1.4-4
12 - AP-42 Table 3.4-3
13 - AP-42 Table 3.4-4
14 - AP-42 Table 3.3-2
15 - AP-42 Table 1.1-12
16 - Engineering Estimate
17 - AP-42 Table 3.1-3
18 - AP-42 Table 3.1-4
19 - AP-42 Table 3.1-5
20 - AP-42 Table 3.1-2a
21 - EPRI, not factor available in AP-42
23 - No. 2 Fuel Oil Sample Submitted January 14, 2010
Note on D14: Lipari, Bernadette: BI wants a all of these changed to 0.0073 lb/MMBtu per TVOP V.B.1.d

## REF 1
JAN | 31 | 0.084932 | TVOP 0056-OP25 Permit Limits
FEB | 28 | 0.076712 | UNIT 1A |  |  | UNITS 2A, 2B, 3 | [5 empty] | COOLING TOWER |  |  |  | DIESEL STARTER ENGINE 1 |  |  |  | DIESEL FIRE PUMP 1
MAR | 31 | 0.084932 | Firing Capacity (MMBtu/hr) | 300 |  | Firing Capacity (MMBtu/hr) | 918
APR | 30 | 0.082192
MAY | 31 | 0.084932
JUN | 30 | 0.082192
JUL | 31 | 0.084932 | Condition V.A.1.m: |  |  | Condition V.B.1.b | [5 empty] | Condition V.C.1.a |  |  |  | Condition V.D - Capacity |  |  |  | Condition V.D - Capacity
AUG | 31 | 0.084932 | Permit limit w/ 5% capacity factor limit | 2170.5942 | gal/hr | Heat input limit to each HRSG duct burner (MMBtu/hr) | 240 |  |  |  |  | Total dissolved solids concentration limit (ppmw) |  | 3327 |  | 3400000 | Btu/hr |  |  | 2100000 | Btu/hr
SEP | 30 | 0.082192 |  | 950720.2755 | gal/12-mo
OCT | 31 | 0.084932 | [13 empty] | Condition V.D.1.a(1) |  |  |  | Condition V.D.1.a(1)
NOV | 30 | 0.082192 | [13 empty] | Sulfur content max (%) | 0.0015 |  |  | Sulfur content max (%) | 0.0015
DEC | 31 | 0.084932 | Table V-A-1: |  | 5% Capacity Factor Annual Emission Limit (tons/year) | Table V-B-1 |  | 3.6 |  | 15.768 |  | Table V-C-1
|  |  |  | Hourly Emission Limit (lb/hr) |  |  | Hourly Emission Limit (lb/hr) 1 | Hourly Emission Limit (lb/hr) | Annual Emission Limit (tons/year) | Annual Emission Limit (tons/year) | Check: Annual Emission Limit (tpy) |  | Daily Emission Limit (lb/day) 1 | Annual Emission Limit (tons/year) |  | 1 OP# 0056; Issed on 2/15/2011
|  |  | Pollutant |  |  | Pollutant | [5 empty] | Pollutant
|  |  | Particulate Matter 1 | 1.5 | 0.3285 | Particulate Matter | 6.7 | 3.6 | 30 | 15.768 | 29.346 | PM | 53.52 | 9.76
|  |  | PM10 1 | 1.5 | 0.3285 | PM10 | 6.7 | 3.6 | 30 | 15.768 | 29.346 | PM10 | 53.52 | 9.76
|  |  | Nitrogen Oxides 2 | 111 | See blo | Nitrogen Oxides (RACT III) | 11.8 |  | 51.7 |  | 51.684 | 1 IP#0056-I001a
|  |  | Sulfur Oxides 3 | 63 | 13.797 | Sulfur Oxides 2 | 2.6 | 0.7 | 11.5 | 3.066 | 11.388
|  |  | Carbon Monoxide 3 | 35.5 | 7.7745 | Carbon Monoxide (90-100% full load) | 40 |  | 175 |  | 175.2 | Objective: | To determine the particulate emissions from the existing cooling
|  |  | Volatile Organic Compounds 2 | 4.1 | See blo | Carbon Monoxide (<90% full load) 3 | 60 | [5 empty] | tower at Brunot Island Power Station.
|  |  | 1 OP#1065009-000-23600/RACT |  |  | Volatile Organic Compounds (RACT III) 3 | 3 |  | 12 |  | 13.14
|  |  | 2 OP#0056-OP19/IP#0056-I002 with Cheswick Ave Plan |  |  | Formaldehyde (90-100% full load) | 0.64 |  | 2.8 |  | 2.8032 | References: | 1. Operating Manual for the Circulating Water System, Brunot Island Station;
|  |  | 3 OP#0056a |  |  | Formaldehyde (<90% full load) | 1.32 | [5 empty] | Marley Cooling Tower Model No. 6516-4-04.
[6 empty] | Ammonia | 14 |  | 61.3 |  | 61.32 |  | 2. Fax dated 11/29/2000 from Marley Cooling Tower Company.
[6 empty] | 1 IP#0056-I001/Manf. Specs./BACT/IP#0056-I001a |  | 0.6864 |  | 3.0064 |  |  | 3. Brunot Island NPDES Permit Renewal Application, November 1999.
|  |  | Table V-A-1a from Installation Permit No. 0056-I002 (w/o averaging plan): |  |  | 2 IP#0056-I001a | [6 empty] | 4. Water Mass Balance, Black & Veatch, Dwgs WMB-4 and WMB-5, 4/21/2000.
|  |  |  | Hourly Emission Limit (lb/hr) 1 | Annual Emission Limit (tons/year) | 3 IP#0056-I001b | [6 empty] | 5. USEPA AP-42 Section 13.4 Wet Cooling Towers.
Pollutant
|  |  | Nitrogen Oxides | 209.4 | 45.8586 | [6 empty] | Assumptions: | Remaining solid particles in the evaporating water are within the
|  |  | Volatile Organic Compounds | 9.22 | 2.0192 | [7 empty] | PM-10 size range, therefore, TSP = PM-10.
1 IP#0056-I002 without Cheswick Ave Plan
[12 empty] | Parameters: |  |  | Design Circulation Rate, C = |  | 84000 | GPM | (Ref. 1)
[15 empty] | Total Liquid Drift, LD = |  | 5e-05 |  | (Ref. 2)
|  |  | IP#0056-I002; Issued on 2/28/2020: | [11 empty] | TDS of Make-up Water = |  | 212 | ppmw | (Ref. 3)
|  |  | Since the termination of the Cheswick Averaging Plan, the NOX limit | [11 empty] | Maximum number of Recycles = |  | 5 |  | (Ref. 4)
|  |  | for the unit is 0.698 lb/MMBtu. | [11 empty] | TDS of Circulating Water, TDS = |  | 1060 | ppmw
|  |  | A 5% capacity factor was used to calculate the | [11 empty] | Density of Water, d = |  | 8.34 | lb/gal
|  |  | annual NOX emissions limit in the TVOP. | [11 empty] | Actual Operating Hours, Ha = |  | 8760 | hrs/yr
Emission limit = (0.698 lb / MMBtu) x (300 MMBtu / hr) = 209.4 lb/hr.
|  |  | Emission limit = (209.4 lb / hr) x (8760 hr / yr) x (5% capacity factor) | [11 empty] | Potential Operating Hours, Hp = |  | 8760 | hrs/yr
|  |  | x (1 ton / 2000 lb) = 45.86 ton/year. | [11 empty] | Number of Cells in Tower = |  | 4 |  | (Ref. 1)
|  |  | OP# 0056; Issed on 2/16/2006: | [8 empty] | Calculation: | (Based on Reference 5)
Allowable VOC = 0.002% of stack gas volume as carbon (20 ppm)
|  |  | (0.00002) x (616,667 acfm ) = 12.33 acfm VOC = 0.0128 moles VOC | [9 empty] | Hourly PM-10/TSP emissions (lb/hr) = C x 60 min/hr x LD x d x (TDS/1E+06)
|  |  | (0.0128 moles VOC/min) x (60 min/hr) x (12 lb VOC/moles) = 9.22 lbs/hr | [9 empty] | Actual annual PM-10/TSP emissions (tpy) = hourly emissions x Ha / 2000 lbs/ton
Potential annual PM-10/TSP emissions (tpy) = hourly emissions x Hp / 2000 lbs/ton
The stack exhaust = 616,667 acfm. Allowable VOC = 0.002% on a wet basis. One mole equals 965 ft3 at exhaust
|  |  | conditions which gives 0.0128 moles VOC per minute. One mole of VOCs as carbon equals 12 pounds. a | [10 empty] | Emission Rates:
|  |  | a OP# 0056 Technical Support Document; Issed on 2/6/2006 | [11 empty] | Hourly PM-10/TSP emissions = |  | 2.2278 | lbs/hr
[15 empty] | Actual annual PM-10/TSP emissions = |  | 9.7577 | tons/yr
|  |  | OP# 0056a; Issed on 3/14/2008: | [11 empty] | Potential annual PM-10/TSP emissions = |  | 9.7577 | tons/yr
Only no.2 fuel oil with a maximum sulfur content of 0.2%
|  |  | Condition V.A.1.a. – Revise 0.5% to 0.2%; Condition V.A.1.g – revised 0.50 lb/MMBtu to 0.21 lb/MMBtu | [11 empty] | Annual PM-10/TSP emissions, per cell = |  | 2.4394 | tons/yr = | 0.070175 | g/s
Condition V.A.1.h. – Revised CO from 0.50 ppm to 50 ppm at 15% O2
Note on F8: Lipari, Bernadette: See 2/24/2024 TVOP application Section 7 pdf p. 120 - 5% capacity factor
Note on K13: Lipari, Bernadette: IP1 limits Mfg Specs/BACT
Note on N13: Lipari, Bernadette: These are from tab Brunot Island PTE from copy0056op2024-02-23app.xls
Note on O15: Lipari, Bernadette: Co. spreadsheet showing this as 15.8, but they are not asking for a change in the permit.
Note on F17: Lipari, Bernadette: The old PA Presumptive RACT NOX limit for the unit is 96 ppmvd @ 15% oxygen (0.37 lb/MMBtu). A 36% capacity factor was used to calculate the annual NOx emissions limit in the TVOP GenOn requesting removal of presumptive cond. b/c of the 5% cap. factor. IP#2 states that these will be replaced by 0.698 lb/MMBtu when the ave plan is terminated. See new calc blo.
Note on K18: Lipari, Bernadette: IP1 limit = 6.2 lb/hr 2019 TVOP limit = 2.6 lb/hr
Note on O18: Lipari, Bernadette: IP1 limit = 27.3 tpy Co. spreadsheet showing this as 3.0, but they are not asking for a change in the permit.
Note on K21: Lipari, Bernadette: Updated calc from BI VOC=2.7 lb/hr but the IP=3 lb/hr
Note on O21: Lipari, Bernadette: IP1a VOC limit=12 tpy
Note on F29: Lipari, Bernadette: See 1A PPM RACT Calcs tab
Note on F30: Lipari, Bernadette: See 1A PPM RACT Calcs tab

## REF 2
Name: |  | Turbine 1A |  |  | Name: |  | Turbine 2A |  |  | Name: |  | Turbine 2B |  |  | Name: |  | Turbine 3 |  |  | Name: |  | Cooling Tower |  |  | Name: |  | Starting Diesel |  |  | Name: |  | Fire Pump
|  |  | Emissions | Calculation |  |  |  | Emissions | Calculation |  |  |  | Emissions | Calculation |  |  |  | Emissions | Calculation |  |  |  | Emissions | Calculation |  |  |  | Emissions | Calculation |  |  |  | Emissions | Calculation
Pollutant | Pollutant Type | CAS | Tons/Year | Method | Pollutant | Pollutant Type | CAS | Tons/Year | Method | Pollutant | Pollutant Type | CAS | Tons/Year | Method | Pollutant | Pollutant Type | CAS | Tons/Year | Method | Pollutant | Pollutant Type | CAS | Tons/Year | Method | Pollutant | Pollutant Type | CAS | Tons/Year | Method | Pollutant | Pollutant Type | CAS | Tons/Year | Method
Ammonia |  | 7664-41-7 | NA | - | Ammonia |  | 7664-41-7 | 61.32 | ACHD calc | Ammonia |  | 7664-41-7 | 61.32 | ACHD calc | Ammonia |  | 7664-41-7 | 61.32 | ACHD calc | Ammonia |  | 7664-41-7 | NA | - | Ammonia |  | 7664-41-7 | NA | - | Ammonia |  | 7664-41-7 | NA | -
CO |  | 630-08-0 | 7.7745 | ACHD TVOP No. 0056 | CO |  | 630-08-0 | 175.2 | ACHD calc | CO |  | 630-08-0 | 175.2 | ACHD calc | CO |  | 630-08-0 | 175.2 | ACHD calc | CO |  | 630-08-0 | NA | - | CO |  | 630-08-0 | 0.8075 | AP-42 | CO |  | 630-08-0 | 0.49875 | AP-42
Lead |  | 7439-92-1 | 0.0009198 | AP-42 | Lead |  | 7439-92-1 | NA | - | Lead |  | 7439-92-1 | NA | - | Lead |  | 7439-92-1 | NA | - | Lead |  | 7439-92-1 | NA | - | Lead |  | 7439-92-1 | NA | - | Lead |  | 7439-92-1 | NA | -
NOx |  | 10102-44-0 | 45.8586 | ACHD TVOP No. 0056 | NOx |  | 10102-44-0 | 51.684 | ACHD calc | NOx |  | 10102-44-0 | 51.684 | ACHD calc | NOx |  | 10102-44-0 | 51.684 | ACHD calc | NOx |  | 10102-44-0 | NA | - | NOx |  | 10102-44-0 | 3.7485 | AP-42 | NOx |  | 10102-44-0 | 2.3152 | AP-42
PM |  |  | 0.3285 | ACHD TVOP No. 0056 | PM |  |  | 15.768 | ACHD TVOP No. 0056 | PM |  |  | 15.768 | ACHD TVOP No. 0056 | PM |  |  | 15.768 | ACHD TVOP No. 0056 | PM |  |  | 9.7577 | ACHD TVOP No. 0056 | PM |  |  | 0.238 | ACHD TVOP No. 0056 | PM |  |  | 0.147 | ACHD TVOP No. 0056
PMCond |  |  | 0.47304 | AP-42 | PMCond |  |  | 4.9406 | AP-42 | PMCond |  |  | 4.9406 | AP-42 | PMCond |  |  | 4.9406 | AP-42 | PMCond |  |  | NA | - | PMCond |  |  | NA | - | PMCond |  |  | NA | -
PM10 |  |  | 0.3285 | ACHD TVOP No. 0056 | PM10 |  |  | 15.768 | ACHD TVOP No. 0056 | PM10 |  |  | 15.768 | ACHD TVOP No. 0056 | PM10 |  |  | 15.768 | ACHD TVOP No. 0056 | PM10 |  |  | 9.7577 | ACHD TVOP No. 0056 | PM10 |  |  | 0.238 | ACHD TVOP No. 0056 | PM10 |  |  | 0.147 | ACHD TVOP No. 0056
PM2.5 |  |  | 0.3285 | Assume equal to PM10 | PM2.5 |  |  | 15.768 | Assume equal to PM10 | PM2.5 |  |  | 15.768 | Assume equal to PM10 | PM2.5 |  |  | 15.768 | Assume equal to PM10 | PM2.5 |  |  | 9.7577 | Assume equal to PM10 | PM2.5 |  |  | 0.238 | - | PM2.5 |  |  | 0.147 | -
SOX |  | 7446-09-5 | 13.797 | ACHD TVOP No. 0056 | SOX |  | 7446-09-5 | 3.0064 | ACHD TVOP No. 0056 | SOX |  | 7446-09-5 | 3.0064 | ACHD TVOP No. 0056 | SOX |  | 7446-09-5 | 3.0064 | ACHD TVOP No. 0056 | SOX |  | 7446-09-5 | NA | - | SOX |  | 7446-09-5 | 0.0013909 | Mass Balance | SOX |  | 7446-09-5 | 0.00085909 | Mass Balance
VOC |  |  | 2.0192 | ACHD TVOP No. 0056 | VOC |  |  | 13.14 | ACHD calc | VOC |  |  | 13.14 | ACHD calc | VOC |  |  | 13.14 | ACHD calc | VOC |  |  | NA | - | VOC |  |  | 0.306 | AP-42 | VOC |  |  | 0.189 | AP-42
1,3 Butadiene | VOC | 106-99-0 | 0.0010512 | AP-42 | 1,3 Butadiene | VOC | 106-99-0 | 0.00045202 | AP-42 | 1,3 Butadiene | VOC | 106-99-0 | 0.00045202 | AP-42 | 1,3 Butadiene | VOC | 106-99-0 | 0.00045202 | AP-42 | 1,3 Butadiene | VOC | 106-99-0 | NA | - | 1,3 Butadiene | VOC | 106-99-0 | 3.3235e-05 | AP-42 | 1,3 Butadiene | VOC | 106-99-0 | 2.0527e-05 | AP-42
1,1,1-Trichloroethane | VOC | 71-55-6 | NA | - | 1,1,1-Trichloroethane | VOC | 71-55-6 | NA | - | 1,1,1-Trichloroethane | VOC | 71-55-6 | NA | - | 1,1,1-Trichloroethane | VOC | 71-55-6 | NA | - | 1,1,1-Trichloroethane | VOC | 71-55-6 | NA | - | 1,1,1-Trichloroethane | VOC | 71-55-6 | NA | - | 1,1,1-Trichloroethane | VOC | 71-55-6 | NA | -
1,2,4-Trimethlybenzene |  | 95-63-6 | NA | - | 1,2,4-Trimethlybenzene |  | 95-63-6 | NA | - | 1,2,4-Trimethlybenzene |  | 95-63-6 | NA | - | 1,2,4-Trimethlybenzene |  | 95-63-6 | NA | - | 1,2,4-Trimethlybenzene |  | 95-63-6 | NA | - | 1,2,4-Trimethlybenzene |  | 95-63-6 | NA | - | 1,2,4-Trimethlybenzene |  | 95-63-6 | NA | -
2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | - | 2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | - | 2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | - | 2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | - | 2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | - | 2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | - | 2,3,7,8 -Tetrachlorodibenzo p dioxin | VOC | 1746-01-6 | NA | -
2,4-Dinitrotoluene | VOC | 121-14-2 | NA | - | 2,4-Dinitrotoluene | VOC | 121-14-2 | NA | - | 2,4-Dinitrotoluene | VOC | 121-14-2 | NA | - | 2,4-Dinitrotoluene | VOC | 121-14-2 | NA | - | 2,4-Dinitrotoluene | VOC | 121-14-2 | NA | - | 2,4-Dinitrotoluene | VOC | 121-14-2 | NA | - | 2,4-Dinitrotoluene | VOC | 121-14-2 | NA | -
2-Chloroacetophenone | VOC | 532-27-4 | NA | - | 2-Chloroacetophenone | VOC | 532-27-4 | NA | - | 2-Chloroacetophenone | VOC | 532-27-4 | NA | - | 2-Chloroacetophenone | VOC | 532-27-4 | NA | - | 2-Chloroacetophenone | VOC | 532-27-4 | NA | - | 2-Chloroacetophenone | VOC | 532-27-4 | NA | - | 2-Chloroacetophenone | VOC | 532-27-4 | NA | -
Acetaldehyde | VOC | 75-07-0 | NA | - | Acetaldehyde | VOC | 75-07-0 | 0.042048 | AP-42 | Acetaldehyde | VOC | 75-07-0 | 0.042048 | AP-42 | Acetaldehyde | VOC | 75-07-0 | 0.042048 | AP-42 | Acetaldehyde | VOC | 75-07-0 | NA | - | Acetaldehyde | VOC | 75-07-0 | 0.00065195 | AP-42 | Acetaldehyde | VOC | 75-07-0 | 0.00040268 | AP-42
Acetophenone | VOC | 98-86-2 | NA | - | Acetophenone | VOC | 98-86-2 | NA | - | Acetophenone | VOC | 98-86-2 | NA | - | Acetophenone | VOC | 98-86-2 | NA | - | Acetophenone | VOC | 98-86-2 | NA | - | Acetophenone | VOC | 98-86-2 | NA | - | Acetophenone | VOC | 98-86-2 | NA | -
Acrolein | VOC | 107-02-8 | NA | - | Acrolein | VOC | 107-02-8 | 0.0067277 | AP-42 | Acrolein | VOC | 107-02-8 | 0.0067277 | AP-42 | Acrolein | VOC | 107-02-8 | 0.0067277 | AP-42 | Acrolein | VOC | 107-02-8 | NA | - | Acrolein | VOC | 107-02-8 | 7.8625e-05 | AP-42 | Acrolein | VOC | 107-02-8 | 4.8563e-05 | AP-42
Antimony | PM | 7440-36-0 | NA | - | Antimony | PM | 7440-36-0 | NA | - | Antimony | PM | 7440-36-0 | NA | - | Antimony | PM | 7440-36-0 | NA | - | Antimony | PM | 7440-36-0 | NA | - | Antimony | PM | 7440-36-0 | NA | - | Antimony | PM | 7440-36-0 | NA | -
Arsenic | PM | 7440-38-2 | 0.0007227 | AP-42 | Arsenic | PM | 7440-38-2 | NA | - | Arsenic | PM | 7440-38-2 | NA | - | Arsenic | PM | 7440-38-2 | NA | - | Arsenic | PM | 7440-38-2 | NA | - | Arsenic | PM | 7440-38-2 | NA | - | Arsenic | PM | 7440-38-2 | NA | -
Benzene | VOC | 1746-01-6 | 0.0036135 | AP-42 | Benzene | VOC | 1746-01-6 | 0.012614 | AP-42 | Benzene | VOC | 1746-01-6 | 0.012614 | AP-42 | Benzene | VOC | 1746-01-6 | 0.012614 | AP-42 | Benzene | VOC | 1746-01-6 | NA | - | Benzene | VOC | 1746-01-6 | 0.00079305 | AP-42 | Benzene | VOC | 1746-01-6 | 0.00048983 | AP-42
Benzyl chloride | VOC | 100-44-7 | NA | - | Benzyl chloride | VOC | 100-44-7 | NA | - | Benzyl chloride | VOC | 100-44-7 | NA | - | Benzyl chloride | VOC | 100-44-7 | NA | - | Benzyl chloride | VOC | 100-44-7 | NA | - | Benzyl chloride | VOC | 100-44-7 | NA | - | Benzyl chloride | VOC | 100-44-7 | NA | -
Beryllium | PM | 7440-41-7 | 2.0367e-05 | AP-42 | Beryllium | PM | 7440-41-7 | NA | - | Beryllium | PM | 7440-41-7 | NA | - | Beryllium | PM | 7440-41-7 | NA | - | Beryllium | PM | 7440-41-7 | NA | - | Beryllium | PM | 7440-41-7 | NA | - | Beryllium | PM | 7440-41-7 | NA | -
Biphenyl | VOC | 92-52-4 | NA | - | Biphenyl | VOC | 92-52-4 | NA | - | Biphenyl | VOC | 92-52-4 | NA | - | Biphenyl | VOC | 92-52-4 | NA | - | Biphenyl | VOC | 92-52-4 | NA | - | Biphenyl | VOC | 92-52-4 | NA | - | Biphenyl | VOC | 92-52-4 | NA | -
Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | - | Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | - | Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | - | Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | - | Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | - | Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | - | Bis(2-ethylhexyl)phthalate (DEHP) | VOC | 117-81-7 | NA | -
Bromoform | VOC | 75-25-2 | NA | - | Bromoform | VOC | 75-25-2 | NA | - | Bromoform | VOC | 75-25-2 | NA | - | Bromoform | VOC | 75-25-2 | NA | - | Bromoform | VOC | 75-25-2 | NA | - | Bromoform | VOC | 75-25-2 | NA | - | Bromoform | VOC | 75-25-2 | NA | -
Cadmium | PM | 7440-43-9 | 0.00031536 | AP-42 | Cadmium | PM | 7440-43-9 | NA | - | Cadmium | PM | 7440-43-9 | NA | - | Cadmium | PM | 7440-43-9 | NA | - | Cadmium | PM | 7440-43-9 | NA | - | Cadmium | PM | 7440-43-9 | NA | - | Cadmium | PM | 7440-43-9 | NA | -
Carbon disulfide | VOC | 75-15-0 | NA | - | Carbon disulfide | VOC | 75-15-0 | NA | - | Carbon disulfide | VOC | 75-15-0 | NA | - | Carbon disulfide | VOC | 75-15-0 | NA | - | Carbon disulfide | VOC | 75-15-0 | NA | - | Carbon disulfide | VOC | 75-15-0 | NA | - | Carbon disulfide | VOC | 75-15-0 | NA | -
Chlorobenzene | VOC | 108-90-7 | NA | - | Chlorobenzene | VOC | 108-90-7 | NA | - | Chlorobenzene | VOC | 108-90-7 | NA | - | Chlorobenzene | VOC | 108-90-7 | NA | - | Chlorobenzene | VOC | 108-90-7 | NA | - | Chlorobenzene | VOC | 108-90-7 | NA | - | Chlorobenzene | VOC | 108-90-7 | NA | -
Chloroform | VOC | 67-66-3 | NA | - | Chloroform | VOC | 67-66-3 | NA | - | Chloroform | VOC | 67-66-3 | NA | - | Chloroform | VOC | 67-66-3 | NA | - | Chloroform | VOC | 67-66-3 | NA | - | Chloroform | VOC | 67-66-3 | NA | - | Chloroform | VOC | 67-66-3 | NA | -
Chromium | PM | 7440-43-7 | 0.0007227 | AP-42 | Chromium | PM | 7440-43-7 | NA | - | Chromium | PM | 7440-43-7 | NA | - | Chromium | PM | 7440-43-7 | NA | - | Chromium | PM | 7440-43-7 | NA | - | Chromium | PM | 7440-43-7 | NA | - | Chromium | PM | 7440-43-7 | NA | -
Cobalt | PM | 7440-48-4 | NA | - | Cobalt | PM | 7440-48-4 | NA | - | Cobalt | PM | 7440-48-4 | NA | - | Cobalt | PM | 7440-48-4 | NA | - | Cobalt | PM | 7440-48-4 | NA | - | Cobalt | PM | 7440-48-4 | NA | - | Cobalt | PM | 7440-48-4 | NA | -
Cumene | VOC | 98-82-8 | NA | - | Cumene | VOC | 98-82-8 | NA | - | Cumene | VOC | 98-82-8 | NA | - | Cumene | VOC | 98-82-8 | NA | - | Cumene | VOC | 98-82-8 | NA | - | Cumene | VOC | 98-82-8 | NA | - | Cumene | VOC | 98-82-8 | NA | -
Cyanide | PM | 57-12-5 | NA | - | Cyanide | PM | 57-12-5 | NA | - | Cyanide | PM | 57-12-5 | NA | - | Cyanide | PM | 57-12-5 | NA | - | Cyanide | PM | 57-12-5 | NA | - | Cyanide | PM | 57-12-5 | NA | - | Cyanide | PM | 57-12-5 | NA | -
Dichlorobenzene | VOC | 25321-22-6 | NA | - | Dichlorobenzene | VOC | 25321-22-6 | NA | - | Dichlorobenzene | VOC | 25321-22-6 | NA | - | Dichlorobenzene | VOC | 25321-22-6 | NA | - | Dichlorobenzene | VOC | 25321-22-6 | NA | - | Dichlorobenzene | VOC | 25321-22-6 | NA | - | Dichlorobenzene | VOC | 25321-22-6 | NA | -
Dimethyl sulfate | VOC | 77-78-1 | NA | - | Dimethyl sulfate | VOC | 77-78-1 | NA | - | Dimethyl sulfate | VOC | 77-78-1 | NA | - | Dimethyl sulfate | VOC | 77-78-1 | NA | - | Dimethyl sulfate | VOC | 77-78-1 | NA | - | Dimethyl sulfate | VOC | 77-78-1 | NA | - | Dimethyl sulfate | VOC | 77-78-1 | NA | -
Dioxins (PCDD) | VOC |  | NA | - | Dioxins (PCDD) | VOC |  | NA | - | Dioxins (PCDD) | VOC |  | NA | - | Dioxins (PCDD) | VOC |  | NA | - | Dioxins (PCDD) | VOC |  | NA | - | Dioxins (PCDD) | VOC |  | NA | - | Dioxins (PCDD) | VOC |  | NA | -
Ethyl benzene | VOC | 100-41-4 | NA | - | Ethyl benzene | VOC | 100-41-4 | 0.033638 | AP-42 | Ethyl benzene | VOC | 100-41-4 | 0.033638 | AP-42 | Ethyl benzene | VOC | 100-41-4 | 0.033638 | AP-42 | Ethyl benzene | VOC | 100-41-4 | NA | - | Ethyl benzene | VOC | 100-41-4 | NA | - | Ethyl benzene | VOC | 100-41-4 | NA | -
Ethyl chloride | VOC | 75-00-3 | NA | - | Ethyl chloride | VOC | 75-00-3 | NA | - | Ethyl chloride | VOC | 75-00-3 | NA | - | Ethyl chloride | VOC | 75-00-3 | NA | - | Ethyl chloride | VOC | 75-00-3 | NA | - | Ethyl chloride | VOC | 75-00-3 | NA | - | Ethyl chloride | VOC | 75-00-3 | NA | -
Ethylene dibromide | VOC | 106-93-4 | NA | - | Ethylene dibromide | VOC | 106-93-4 | NA | - | Ethylene dibromide | VOC | 106-93-4 | NA | - | Ethylene dibromide | VOC | 106-93-4 | NA | - | Ethylene dibromide | VOC | 106-93-4 | NA | - | Ethylene dibromide | VOC | 106-93-4 | NA | - | Ethylene dibromide | VOC | 106-93-4 | NA | -
Ethylene dichloride | VOC | 107-06-2 | NA | - | Ethylene dichloride | VOC | 107-06-2 | NA | - | Ethylene dichloride | VOC | 107-06-2 | NA | - | Ethylene dichloride | VOC | 107-06-2 | NA | - | Ethylene dichloride | VOC | 107-06-2 | NA | - | Ethylene dichloride | VOC | 107-06-2 | NA | - | Ethylene dichloride | VOC | 107-06-2 | NA | -
Ethylene glycol | VOC | 107-21-1 | NA | - | Ethylene glycol | VOC | 107-21-1 | NA | - | Ethylene glycol | VOC | 107-21-1 | NA | - | Ethylene glycol | VOC | 107-21-1 | NA | - | Ethylene glycol | VOC | 107-21-1 | NA | - | Ethylene glycol | VOC | 107-21-1 | NA | - | Ethylene glycol | VOC | 107-21-1 | NA | -
Formaldehyde | VOC | 50-00-0 | 0.018396 | AP-42 | Formaldehyde | VOC | 50-00-0 | 2.8032 | ACHD calc | Formaldehyde | VOC | 50-00-0 | 2.8032 | ACHD calc | Formaldehyde | VOC | 50-00-0 | 2.8032 | ACHD calc | Formaldehyde | VOC | 50-00-0 | NA | - | Formaldehyde | VOC | 50-00-0 | 0.001003 | AP-42 | Formaldehyde | VOC | 50-00-0 | 0.0006195 | AP-42
Furans (PCDF) | VOC | 132-64-9 | NA | - | Furans (PCDF) | VOC | 132-64-9 | NA | - | Furans (PCDF) | VOC | 132-64-9 | NA | - | Furans (PCDF) | VOC | 132-64-9 | NA | - | Furans (PCDF) | VOC | 132-64-9 | NA | - | Furans (PCDF) | VOC | 132-64-9 | NA | - | Furans (PCDF) | VOC | 132-64-9 | NA | -
Hexane | VOC | 110-54-3 | NA | - | Hexane | VOC | 110-54-3 | NA | - | Hexane | VOC | 110-54-3 | NA | - | Hexane | VOC | 110-54-3 | NA | - | Hexane | VOC | 110-54-3 | NA | - | Hexane | VOC | 110-54-3 | NA | - | Hexane | VOC | 110-54-3 | NA | -
Hydrochloric acid | Acids | 7647-01-0 | 0.021867 | Fuel Data | Hydrochloric acid | Acids | 7647-01-0 | NA | - | Hydrochloric acid | Acids | 7647-01-0 | NA | - | Hydrochloric acid | Acids | 7647-01-0 | NA | - | Hydrochloric acid | Acids | 7647-01-0 | NA | - | Hydrochloric acid | Acids | 7647-01-0 | 2.3675e-05 | AP-42 | Hydrochloric acid | Acids | 7647-01-0 | 1.4623e-05 | AP-42
Hydrofluoric acid | Acids | 7664-39-3 | NA | - | Hydrofluoric acid | Acids | 7664-39-3 | NA | - | Hydrofluoric acid | Acids | 7664-39-3 | NA | - | Hydrofluoric acid | Acids | 7664-39-3 | NA | - | Hydrofluoric acid | Acids | 7664-39-3 | NA | - | Hydrofluoric acid | Acids | 7664-39-3 | NA | - | Hydrofluoric acid | Acids | 7664-39-3 | NA | -
Isophorone | VOC | 78-59-1 | NA | - | Isophorone | VOC | 78-59-1 | NA | - | Isophorone | VOC | 78-59-1 | NA | - | Isophorone | VOC | 78-59-1 | NA | - | Isophorone | VOC | 78-59-1 | NA | - | Isophorone | VOC | 78-59-1 | NA | - | Isophorone | VOC | 78-59-1 | NA | -
Manganese | PM | 7439-96-5 | 0.051903 | AP-42 | Manganese | PM | 7439-96-5 | NA | - | Manganese | PM | 7439-96-5 | NA | - | Manganese | PM | 7439-96-5 | NA | - | Manganese | PM | 7439-96-5 | NA | - | Manganese | PM | 7439-96-5 | NA | - | Manganese | PM | 7439-96-5 | NA | -
Mercury | PM | 7439-97-6 | 7.884e-05 | AP-42 | Mercury | PM | 7439-97-6 | NA | - | Mercury | PM | 7439-97-6 | NA | - | Mercury | PM | 7439-97-6 | NA | - | Mercury | PM | 7439-97-6 | NA | - | Mercury | PM | 7439-97-6 | NA | - | Mercury | PM | 7439-97-6 | NA | -
Methyl bromide | VOC | 74-83-9 | NA | - | Methyl bromide | VOC | 74-83-9 | NA | - | Methyl bromide | VOC | 74-83-9 | NA | - | Methyl bromide | VOC | 74-83-9 | NA | - | Methyl bromide | VOC | 74-83-9 | NA | - | Methyl bromide | VOC | 74-83-9 | NA | - | Methyl bromide | VOC | 74-83-9 | NA | -
Methyl chloride | VOC | 74-87-3 | NA | - | Methyl chloride | VOC | 74-87-3 | NA | - | Methyl chloride | VOC | 74-87-3 | NA | - | Methyl chloride | VOC | 74-87-3 | NA | - | Methyl chloride | VOC | 74-87-3 | NA | - | Methyl chloride | VOC | 74-87-3 | NA | - | Methyl chloride | VOC | 74-87-3 | NA | -
Methyl hydrazine | VOC | 60-34-4 | NA | - | Methyl hydrazine | VOC | 60-34-4 | NA | - | Methyl hydrazine | VOC | 60-34-4 | NA | - | Methyl hydrazine | VOC | 60-34-4 | NA | - | Methyl hydrazine | VOC | 60-34-4 | NA | - | Methyl hydrazine | VOC | 60-34-4 | NA | - | Methyl hydrazine | VOC | 60-34-4 | NA | -
Methyl methacrylate | VOC | 80-62-6 | NA | - | Methyl methacrylate | VOC | 80-62-6 | NA | - | Methyl methacrylate | VOC | 80-62-6 | NA | - | Methyl methacrylate | VOC | 80-62-6 | NA | - | Methyl methacrylate | VOC | 80-62-6 | NA | - | Methyl methacrylate | VOC | 80-62-6 | NA | - | Methyl methacrylate | VOC | 80-62-6 | NA | -
Methyl tert butyl ether | VOC | 1634-04-4 | NA | - | Methyl tert butyl ether | VOC | 1634-04-4 | NA | - | Methyl tert butyl ether | VOC | 1634-04-4 | NA | - | Methyl tert butyl ether | VOC | 1634-04-4 | NA | - | Methyl tert butyl ether | VOC | 1634-04-4 | NA | - | Methyl tert butyl ether | VOC | 1634-04-4 | NA | - | Methyl tert butyl ether | VOC | 1634-04-4 | NA | -
Methylene chloride | VOC | 75-09-2 | NA | - | Methylene chloride | VOC | 75-09-2 | NA | - | Methylene chloride | VOC | 75-09-2 | NA | - | Methylene chloride | VOC | 75-09-2 | NA | - | Methylene chloride | VOC | 75-09-2 | NA | - | Methylene chloride | VOC | 75-09-2 | NA | - | Methylene chloride | VOC | 75-09-2 | NA | -
Naphthalene | VOC | 91-20-3 | 0.0022995 | AP-42 | Naphthalene | VOC | 91-20-3 | 0.0013666 | AP-42 | Naphthalene | VOC | 91-20-3 | 0.0013666 | AP-42 | Naphthalene | VOC | 91-20-3 | 0.0013666 | AP-42 | Naphthalene | VOC | 91-20-3 | NA | - | Naphthalene | VOC | 91-20-3 | 7.208e-05 | AP-42 | Naphthalene | VOC | 91-20-3 | 4.452e-05 | AP-42
Nickel | PM | 7440-02-0 | 0.00030222 | AP-42 | Nickel | PM | 7440-02-0 | NA | - | Nickel | PM | 7440-02-0 | NA | - | Nickel | PM | 7440-02-0 | NA | - | Nickel | PM | 7440-02-0 | NA | - | Nickel | PM | 7440-02-0 | NA | - | Nickel | PM | 7440-02-0 | NA | -
Phenol | VOC | 108-95-2 | NA | - | Phenol | VOC | 108-95-2 | NA | - | Phenol | VOC | 108-95-2 | NA | - | Phenol | VOC | 108-95-2 | NA | - | Phenol | VOC | 108-95-2 | NA | - | Phenol | VOC | 108-95-2 | NA | - | Phenol | VOC | 108-95-2 | NA | -
Polycyclic Organic Matter | VOC |  | 0.0003285 | AP-42 | Polycyclic Organic Matter | VOC |  | 0.00094608 | AP-42 | Polycyclic Organic Matter | VOC |  | 0.00094608 | AP-42 | Polycyclic Organic Matter | VOC |  | 0.00094608 | AP-42 | Polycyclic Organic Matter | VOC |  | NA | - | Polycyclic Organic Matter | VOC |  | 7.072e-05 | AP-42 | Polycyclic Organic Matter | VOC |  | 4.368e-05 | AP-42
Propionaldehyde | VOC | 123-38-6 | NA | - | Propionaldehyde | VOC | 123-38-6 | NA | - | Propionaldehyde | VOC | 123-38-6 | NA | - | Propionaldehyde | VOC | 123-38-6 | NA | - | Propionaldehyde | VOC | 123-38-6 | NA | - | Propionaldehyde | VOC | 123-38-6 | NA | - | Propionaldehyde | VOC | 123-38-6 | NA | -
Propylene oxide | VOC | 76-56-9 | NA | - | Propylene oxide | VOC | 76-56-9 | 0.030485 | AP-42 | Propylene oxide | VOC | 76-56-9 | 0.030485 | AP-42 | Propylene oxide | VOC | 76-56-9 | 0.030485 | AP-42 | Propylene oxide | VOC | 76-56-9 | NA | - | Propylene oxide | VOC | 76-56-9 | NA | - | Propylene oxide | VOC | 76-56-9 | NA | -
Selenium | PM | 7782-49-2 | 0.0016425 | AP-42 | Selenium | PM | 7782-49-2 | NA | - | Selenium | PM | 7782-49-2 | NA | - | Selenium | PM | 7782-49-2 | NA | - | Selenium | PM | 7782-49-2 | NA | - | Selenium | PM | 7782-49-2 | NA | - | Selenium | PM | 7782-49-2 | NA | -
Styrene | VOC | 100-42-5 | NA | - | Styrene | VOC | 100-42-5 | NA | - | Styrene | VOC | 100-42-5 | NA | - | Styrene | VOC | 100-42-5 | NA | - | Styrene | VOC | 100-42-5 | NA | - | Styrene | VOC | 100-42-5 | NA | - | Styrene | VOC | 100-42-5 | NA | -
Tetrachloroethylene | VOC | 127-18-4 | NA | - | Tetrachloroethylene | VOC | 127-18-4 | NA | - | Tetrachloroethylene | VOC | 127-18-4 | NA | - | Tetrachloroethylene | VOC | 127-18-4 | NA | - | Tetrachloroethylene | VOC | 127-18-4 | NA | - | Tetrachloroethylene | VOC | 127-18-4 | NA | - | Tetrachloroethylene | VOC | 127-18-4 | NA | -
Toluene | VOC | 108-88-3 | NA | - | Toluene | VOC | 108-88-3 | 0.13666 | AP-42 | Toluene | VOC | 108-88-3 | 0.13666 | AP-42 | Toluene | VOC | 108-88-3 | 0.13666 | AP-42 | Toluene | VOC | 108-88-3 | NA | - | Toluene | VOC | 108-88-3 | 0.00034765 | AP-42 | Toluene | VOC | 108-88-3 | 0.00021473 | AP-42
Vinyl acetate | VOC | 108-05-4 | NA | - | Vinyl acetate | VOC | 108-05-4 | NA | - | Vinyl acetate | VOC | 108-05-4 | NA | - | Vinyl acetate | VOC | 108-05-4 | NA | - | Vinyl acetate | VOC | 108-05-4 | NA | - | Vinyl acetate | VOC | 108-05-4 | NA | - | Vinyl acetate | VOC | 108-05-4 | NA | -
Xylenes | VOC | 1330-20-7 | NA | - | Xylenes | VOC | 1330-20-7 | 0.067277 | AP-42 | Xylenes | VOC | 1330-20-7 | 0.067277 | AP-42 | Xylenes | VOC | 1330-20-7 | 0.067277 | AP-42 | Xylenes | VOC | 1330-20-7 | NA | - | Xylenes | VOC | 1330-20-7 | 0.00024225 | AP-42 | Xylenes | VOC | 1330-20-7 | 0.00014962 | AP-42
Dioxins and Furans in lbs/yr. |  |  |  |  | Dioxins and Furans in lbs/yr. |  |  |  |  | Dioxins and Furans in lbs/yr. |  |  |  |  | Dioxins and Furans in lbs/yr. |  |  |  |  | Dioxins and Furans in lbs/yr. |  |  |  |  | Dioxins and Furans in lbs/yr. |  |  |  |  | Dioxins and Furans in lbs/yr.
NA - No Factor Available. |  |  |  |  | NA - No Factor Available. |  |  |  |  | NA - No Factor Available. |  |  |  |  | NA - No Factor Available. |  |  |  |  | NA - No Factor Available. |  |  |  |  | NA - No Factor Available. |  |  |  |  | NA - No Factor Available.
|  | Total VOC HAPs | 0.025689 |  |  |  | Total VOC HAPs | 3.1049 |  |  |  | Total VOC HAPs | 3.1049 |  |  |  | Total VOC HAPs | 3.1049 |  |  |  | Total VOC HAPs | 0 |  |  |  | Total VOC HAPs | 0.0032926 |  |  |  | Total VOC HAPs | 0.0020336
|  | VOC HAPs > VOC? | No |  |  |  | VOC HAPs > VOC? | No |  |  |  | VOC HAPs > VOC? | No |  |  |  | VOC HAPs > VOC? | No
|  | Total HAP (incl. CH2O) | 0.10326 |  |  |  | Total HAP (incl. CH2O) | 3.1354 |  |  |  | Total HAP (incl. CH2O) | 3.1354 |  |  |  | Total HAP (incl. CH2O) | 3.1354 |  |  |  | Total HAP (incl. CH2O) | 0 |  |  |  | Total HAP (incl. CH2O) | 0.0033162 |  |  |  | Total HAP (incl. CH2O) | 0.0020483
|  | Total Inorganic HAP | 0.077574 |  |  |  | Total Inorganic HAP | 0.030485 |  |  |  | Total Inorganic HAP | 0.030485 |  |  |  | Total Inorganic HAP | 0.030485 |  |  |  | Total Inorganic HAP | 0 |  |  |  | Total Inorganic HAP | 2.3675e-05 |  |  |  | Total Inorganic HAP | 1.4623e-05

## 1A PPM RACT Calcs
Unit 1A
Convert from lb/MMBtu to ppm for NOx (oil firing)
(ERG Calculation Method)
Input |  | Inputs Required in the Conversion
0.698 | lb/MMBtu | 15 | Oxygen (%)
|  | 9190 | Fd (dcf/MMBtu); See EPA Method 19 http://www.epa.gov/ttn/emc/
|  | 1.197e-07 | NOx Conversion factor (lb/scf/ppm); See EPRI Publication (page 135 of 142) http://www.epri.com/abstracts/Pages/ProductAbstract.aspx?ProductId=000000000001011341
PPM Output
179.1231 | ppm at 15% Oxygen | Note: This does not meet the RACT III presumptive limit of 96 ppm.
However, it does meet 25 Pa Code 129.112(c) 9 (ii) of less than 5% capacity.
Convert from lb/MMBtu to ppm for THC (oil firing)
Total VOC is often referred as total hydrocarbon (THC).
Input |  | Inputs Required in the Conversion
0.0307 | lb/MMBtu (the same as the current operating permit) | 1.1419e-07 | THC Conversion factor (lb/scf/ppm); Calculated from an assumed molecular weight
PPM Output
8.2585 | ppm at 15% Oxygen | Note: This meets the RACT presumptive limit of 9 ppm.
| ACHD Calculation Method (RACT II PPMs) | [11 empty] | ACHD Calculation Method (RACT III PPMs)
| Brunot Island Unit 1A | [11 empty] | Brunot Island Unit 1A
300 | Capacity of Each SC Turbine (MMBtu/hr) | [10 empty] | 300 | Capacity of Each SC Turbine (MMBtu/hr)
3153.6 | hours | [10 empty] | 438 | hours
Convert from ppm to lb/MMBtu for NOx (oil firing) | [11 empty] | Convert from ppm to lb/MMBtu for NOx (oil firing)
96 | ppm at % Oxygen | [10 empty] | 179 | ppm at % Oxygen | Note: This does not meet the RACT III presumptive limit of 96 ppm. | Notes:
15 | % Oxygen | [10 empty] | 15 | % Oxygen | However, it does meet 25 Pa Code 129.112(c) 9 (ii) of less than 5% capacity. | 25 Pa Code 129.112(c) 9 (ii)
9190 | Fd - dscf/MMBtu | (Fd (dcf/MMBtu); See EPA Method 19 http://www.epa.gov/ttn/emc/) ?? | [9 empty] | 9190 | Fd - dscf/MMBtu | [5 empty] | [12-month rolling power generation for all units (in MWH)] x 100
1.197e-07 | lb/scf/ppm | (NOx Conversion factor (lb/scf/ppm); See EPRI Publication (page 135 of 142) | [9 empty] | 1.197e-07 | lb/scf/ppm |  | 22 | Capacity of Each SC Turbine (MW) | [Maximum electrical capacity (in MW)] x 8760 hrs
|  | http://www.epri.com/abstracts/Pages/ProductAbstract.aspx?ProductId=000000000001011341) ?? | [12 empty] | 438 | annual (hours) @ 5% capacity
0.37409 | lb/MMBtu | [10 empty] | 0.69752 | lb/MMBtu |  |  |  |  | 5 | %
Note:
112.2268 | lb/hr | [10 empty] | 209.2561 | lb/hr |  | https://pknergypower.com/difference-between-mw-and-mwh/
491.5532 | ton/yr | [10 empty] | 916.5419 | ton/yr |  | MW:If a power plant has a capacity of 10 MW, it can generate
176.9592 | ton/yr (36% capacity factor) | [10 empty] | 45.8271 | ton/yr (5% capacity factor) |  | 10 megawatts of power at any given time.
MWh:If the same power plant operates for 1 hour, it will generate
10 MWh of energy. In other words, MWh is the result of multiplying MW
by time (hours).
Convert from ppm to lb/MMBtu for THC (oil firing) | [11 empty] | Convert from ppm to lb/MMBtu for THC (oil firing)
9 | ppm at % Oxygen | [10 empty] | 8.3 | ppm at % Oxygen | Note: This meets the RACT presumptive limit of 9 ppm.
15 | % Oxygen | [10 empty] | 15 | % Oxygen
9190 | Fd - dscf/MMBtu | [10 empty] | 9190 | Fd - dscf/MMBtu
1.1419e-07 | lb/scf/ppm | (THC Conversion factor (lb/scf/ppm); Calculated from an assumed molecular weight) ?? | [9 empty] | 1.1419e-07 | lb/scf/ppm
0.033456 | lb/MMBtu | [10 empty] | 0.030854 | lb/MMBtu
10.0369 | lb/hr | [10 empty] | 9.2563 | lb/hr
43.9618 | ton/yr | [10 empty] | 40.5426 | ton/yr
15.8263 | ton/yr (36% capacity factor) | [10 empty] | 2.0271 | ton/yr (5% capacity factor)
Past Permit Limit Reference Table
Unit 1A
|  | 300 | MMBtu/hr | 2006 TVOP | 2008 TVOP | 2011 TVOP | 2019 TVOP |  | IP2 R2 |  | 2025 TVOP | R3
|  | 36% | capacity | [5 empty] | w/ave | w/o ave
|  | NOx | lb/MMBtu | 0.698 | 0.698 | 0.698 | 0.37 |  | 0.37 | 0.698 | 0.698 | 0.698
|  |  | lb/hr | 209.4 | 209.4 | 209.4 | 110 |  | 110 | 209.4 | 209.4 | 209.4
|  |  | tpy | 275.2 | 330.2 | 330.2 | 175 |  | 175 | 45.9 | 45.9 | 45.9
|  | VOC | lb/hr | 9.22 | 9.22 | 9.22 | 4.1 |  | 4.1 | 9.22 | 9.22 | 9.22
|  |  | tpy | 14.54 | 14.54 | 14.54 | 6.54 |  | 6.54 | 2 | 2 | 2
Units 2A, 2B, 3
|  | 678 | MMBtu/hr | 2006 TVOP | 2008 TVOP | 2011 TVOP | 2019 TVOP |  |  |  | 2025 TVOP | R3
|  | 918 (ea) | MMBtu/hr
|  | >60% | full load
|  | NOx | lb/hr (ea.) | 11.8 | 11.8 | 11.8 | 11.8 |  |  |  | 11.8 | 11.8
|  |  | tpy (ea.) | 51.7 | 51.7 | 51.7 | 51.7 |  |  |  | 51.7 | 51.7
|  | VOC | lb/hr (ea.) | 3 | 3 | 3 | 3 |  |  |  | 3 | 3
|  |  | tpy (ea.) | 12 | 12 | 12 | 12 |  |  |  | 12 | 12
|  | Units 2A, 2B, 3 |  | IP1 | IP1a | IP1b | IP1c | IP2 | IP2 R2
|  | 918 (ea) | MMBtu/hr
|  | >60% | full load |  | 100% | 100% | 100% | -
|  | NOx | lb/hr (ea.) | 11.8 | 11.8 | 11.8 | 11.8 | - | 11.8
|  |  | tpy (ea.) | 51.7 | 51.7 | 51.7 | 51.7 | - | 51.7
|  | VOC | lb/hr (ea.) | 3 | 3 | 3 | 3 | - | 3
|  |  | tpy (ea.) | 12 | 12 | 12 | 12 | - | 12
Note on C39: Lipari, Bernadette: This matches GeOn's 01-24-2023 R3 Supplemantal letter to ACHD
Note on P39: Lipari, Bernadette: This matches GeOn's 01-24-2023 R3 Supplemantal letter to ACHD
Note on C56: Lipari, Bernadette: Would be closer to permit number of 9.22 if 8.3 is input into ppm
Note on G68: Lipari, Bernadette: from the 2006 tvrv - 0.698 lb/mmbtu; 209.4 lb/hr, and 275.2 tpy is from RACT Order 260
Note on L68: Lipari, Bernadette: Cond. V.A.1.e: shall not exceed 96 ppmvd @ 15% O2 = 0.37 lb/MMBtu
Note on H70: Lipari, Bernadette: per 2008 tvrva - this number is from using the allowable 36% capacity factor
Note on G71: Lipari, Bernadette: See note f from emissions summary table from 2006 TVrv and OP#1065009-000-23600

## 2A, 2B, 3 PPM RACT Calcs
Units 2A, 2B, & 3
Convert from lb/MMBtu to ppm for NOx (NG firing)
(ERG Calculation Method)
| New RACT Limit |  | Inputs Required in the Conversion
| 0.0129 | lb/MMBtu | 15 | Oxygen (%)
|  |  | 9190 | Fd (dcf/MMBtu); See EPA Method 19 http://www.epa.gov/ttn/emc/
|  |  | 1.197e-07 | NOx Conversion factor (lb/scf/ppm); See EPRI Publication (page 135 of 142) http://www.epri.com/abstracts/Pages/ProductAbstract.aspx?ProductId=000000000001011341
| 3.3104 | ppm at 15% Oxygen (a)
(a) Less restrictive than the current operating permit limit i.e., 3.5 ppm
Convert from lb/MMBtu to ppm for THC (NG firing)
Total VOC is often referred as total hydrocarbon (THC).
| New RACT Limit |  | Inputs Required in the Conversion
| 0.003268 | lb/MMBtu (the same as the current operating permit) | 1.1419e-07 | THC Conversion factor (lb/scf/ppm); Calculated from an assumed molecular weight
| 0.8791 | ppm at 15% Oxygen
|  | ACHD Calculation Method (RACT II Presumptive PPMs) |  |  |  | ACHD Calculation Method (RACT II Actual PPMs based off lb/MMBtu) | [8 empty] | ACHD Calculation Method (RACT III Prersumptive PPMs) |  |  |  |  | ACHD Calculation Method (RACT III Actual PPMs based off lb/MMBtu)
|  | Brunot Island Units 2A, 2B, & 3 | HV= | 1038 | btu/scf | [9 empty] | Brunot Island Units 2A, 2B, & 3 |  | HV= | 1038 | btu/scf
|  |  |  | 7747 | MMcf | [12 empty] | 7747 | MMcf
| 918 | Capacity of Each CC Turbine (MMBtu/hr) |  |  |  | 918 | Capacity of Each CC Turbine (MMBtu/hr) | [6 empty] | 918 | Capacity of Each CC Turbine (MMBtu/hr)
| 8760 | hours |  |  |  | 8760 | hours | [6 empty] | 8760 | hours
| Convert from ppm to lb/MMBtu for NOx (NG firing) |  |  |  |  | Convert from lb/MMBtu to ppm for NOx (NG firing) | [7 empty] | Convert from ppm to lb/MMBtu for NOx (NG firing) | [5 empty] | Convert from lb/MMBtu to ppm for NOx (NG firing)
| 42 | ppm at % Oxygen |  |  |  | 0.013 | lb/MMBtu |  |  | 0.16 | lb/MMBtu |  |  | 42 | ppm at % Oxygen |  |  |  |  | 0.0129 | lb/MMBtu |  | 0.16 | lb/MMBtu
| 15 | % Oxygen |  |  |  | 15 | % Oxygen |  |  | 15 | % Oxygen |  |  | 15 | % Oxygen |  |  |  |  | 15 | % Oxygen |  | 15 | % Oxygen
| 8710 | Fd - dscf/MMBtu |  |  |  | 8710 | Fd - dcf/MMBtu |  |  | 8710 | Fd - dcf/MMBtu |  |  | 8710 | Fd - dscf/MMBtu |  |  |  |  | 8710 | Fd - dcf/MMBtu |  | 8710 | Fd - dcf/MMBtu
| 1.197e-07 | lb/scf/ppm |  |  |  | 1.197e-07 | lb/scf/ppm |  |  | 1.197e-07 | lb/scf/ppm |  |  | 1.197e-07 | lb/scf/ppm |  |  |  |  | 1.197e-07 | lb/scf/ppm |  | 1.197e-07 | lb/scf/ppm
Actual:
0.0129 | 0.15512 | lb/MMBtu |  |  |  | 3.52 | ppm at % Oxygen chosen |  |  | 43.3225 | ppm at % Oxygen chosen |  |  | 0.15512 | lb/MMBtu |  |  |  |  | 3.4929 | ppm at % Oxygen chosen |  | 43.3225 | ppm at % Oxygen chosen | Note: This meets the RACT presumptive limit of 42 ppm.
[6 empty] | 3.536 | [13 empty] | 3.5088
11.8 | 142.3962 | NOX Emissions for Each CC Turbine (lb/hr) |  |  |  | Calc check using conversion factors in EPRI document. | [7 empty] | 142.3962 | NOX Emissions for Each CC Turbine (lb/hr) |  |  |  |  | Calc check using conversion factors in EPRI document.
51.7 | 623.6956 | NOX Emissions for Each CC Turbine (ton/yr) | [11 empty] | 623.6956 | NOX Emissions for Each CC Turbine (ton/yr)
[6 empty] | 11.934 | NOX (lb/hr) ea. CC Turbine |  |  | 146.88 | NOX (lb/hr) ea. CC Turbine | [8 empty] | 11.8422 | NOX (lb/hr) ea. CC Turbine |  | 146.88 | NOX (lb/hr) ea. CC Turbine
[6 empty] | 52.2709 | NOX (ton/yr) ea. CC Turbine |  |  | 643.3344 | NOX (ton/yr) ea. CC Turbine | [8 empty] | 51.8688 | NOX (ton/yr) ea. CC Turbine |  | 643.3344 | NOX (ton/yr) ea. CC Turbine
| Convert from ppm to lb/MMBtu for THC (NG firing) |  |  |  |  | Convert from lb/MMBtu to ppm for THC (NG firing) | [7 empty] | Convert from ppm to lb/MMBtu for THC (NG firing) | [5 empty] | Convert from lb/MMBtu to ppm for THC (NG firing)
| 5 | ppm at % Oxygen |  |  |  | 0.0033 | lb/MMBtu |  |  | 0.003 | lb/MMBtu |  |  | 5 | ppm at % Oxygen |  |  |  |  | 0.0033 | lb/MMBtu |  | 0.003 | lb/MMBtu
| 15 | % Oxygen |  |  |  | 15 | % Oxygen |  |  | 15 | % Oxygen |  |  | 15 | % Oxygen |  |  |  |  | 15 | % Oxygen |  | 15 | % Oxygen
| 8710 | Fd - dscf/MMBtu |  |  |  | 8710 | Fd - dcf/MMBtu |  |  | 8710 | Fd - dcf/MMBtu |  |  | 8710 | Fd - dscf/MMBtu |  |  |  |  | 8710 | Fd - dcf/MMBtu |  | 8710 | Fd - dcf/MMBtu
| 1.1419e-07 | lb/scf/ppm |  |  |  | 1.1419e-07 | lb/scf/ppm |  | -OR- | 1.1419e-07 | lb/scf/ppm |  |  | 1.1419e-07 | lb/scf/ppm |  |  |  |  | 1.1419e-07 | lb/scf/ppm | -OR- | 1.1419e-07 | lb/scf/ppm
Actual:
0.003 | 0.017616 | lb/MMBtu |  |  |  | 0.93664 | ppm at % Oxygen chosen |  |  | 0.85149 | ppm at % Oxygen chosen |  |  | 0.017616 | lb/MMBtu |  |  |  |  | 0.93664 | ppm at % Oxygen chosen |  | 0.85149 | ppm at % Oxygen chosen | Note: This meets the RACT presumptive limit of 5 ppm.
[6 empty] | 3.0294 | THC (lb/hr) ea. CC Turbine |  |  | 2.754 | THC (lb/hr) ea. CC Turbine | [8 empty] | 3.0294 | THC (lb/hr) ea. CC Turbine |  | 2.754 | THC (lb/hr) ea. CC Turbine
2.7/3.0 | 16.1716 | THC Emissions for Each CC Turbine (lb/hr) |  |  |  | 13.2688 | THC (ton/yr) ea. CC Turbine |  |  | 12.0625 | THC (ton/yr) ea. CC Turbine |  |  | 16.1716 | THC Emissions for Each CC Turbine (lb/hr) |  |  |  |  | 13.2688 | THC (ton/yr) ea. CC Turbine |  | 12.0625 | THC (ton/yr) ea. CC Turbine
12 | 70.8316 | THC Emissions for Each CC Turbine (ton/yr) | [11 empty] | 70.8316 | THC Emissions for Each CC Turbine (ton/yr)
| NOTE: These are tpy limits based on RACT II presumtive limits of 42 ppm | [12 empty] | NOTE: These are tpy limits based on RACT II presumtive limits of 42 ppm
| and 5 pmm, these are not the actual ppms for the units - see right column for actual | [12 empty] | and 5 pmm, these are not the actual ppms for the units - see right column for actual
Past Permit Limit Reference Table
Unit 1A
[5 empty] | 300 | MMBtu/hr | 2006 TVOP | 2008 TVOP | 2011 TVOP | 2019 TVOP |  | IP2 R2 |  |  | 2025 TVOP | R3
[5 empty] | 36% | capacity | [5 empty] | w/ave | w/o ave
[5 empty] | NOx | lb/MMBtu | 0.698 | 0.698 | 0.698 | 0.37 |  | 0.37 | 0.698 |  | 0.698 | 0.698
[6 empty] | lb/hr | 209.4 | 209.4 | 209.4 | 110 |  | 110 | 209.4 |  | 209.4 | 209.4
[6 empty] | tpy | 275.2 | 330.2 | 330.2 | 175 |  | 175 | 45.9 |  | 45.9 | 45.9
[5 empty] | VOC | lb/hr | 9.22 | 9.22 | 9.22 | 4.1 |  | 4.1 | 9.22 |  | 9.22 | 9.22
[6 empty] | tpy | 14.54 | 14.54 | 14.54 | 6.54 |  | 6.54 | 2 |  | 2 | 2
Units 2A, 2B, 3
[5 empty] | 678 | MMBtu/hr | 2006 TVOP | 2008 TVOP | 2011 TVOP | 2019 TVOP |  |  |  |  | 2025 TVOP | R3
[5 empty] | 918 (ea) | MMBtu/hr
[5 empty] | >60% | full load
[5 empty] | NOx | lb/hr (ea.) | 11.8 | 11.8 | 11.8 | 11.8 |  |  |  |  | 11.8 | 11.8
[6 empty] | tpy (ea.) | 51.7 | 51.7 | 51.7 | 51.7 |  |  |  |  | 51.7 | 51.7
[5 empty] | VOC | lb/hr (ea.) | 3 | 3 | 3 | 3 |  |  |  |  | 3 | 3
[6 empty] | tpy (ea.) | 12 | 12 | 12 | 12 |  |  |  |  | 12 | 12
[5 empty] | Units 2A, 2B, 3 |  | IP1 | IP1a | IP1b | IP1c | IP2 | IP2 R2
[5 empty] | 918 (ea) | MMBtu/hr
[5 empty] | >60% | full load |  | 100% | 100% | 100% | -
[5 empty] | NOx | lb/hr (ea.) | 11.8 | 11.8 | 11.8 | 11.8 | - | 11.8
[6 empty] | tpy (ea.) | 51.7 | 51.7 | 51.7 | 51.7 | - | 51.7
[5 empty] | VOC | lb/hr (ea.) | 3 | 3 | 3 | 3 | - | 3
[6 empty] | tpy (ea.) | 12 | 12 | 12 | 12 | - | 12
Note on H34: Lipari, Bernadette: > 60% load See ract rv2 doc
Note on L34: Lipari, Bernadette: < 60% load with ave. plan See ract rv2 doc
Note on X34: Lipari, Bernadette: > 60% load
Note on AB34: Lipari, Bernadette: < 60% load with ave. plan
Note on C39: Lipari, Bernadette: This matches GeOn's 01-24-2023 R3 Supplemantal letter to ACHD
Note on L39: Lipari, Bernadette: Slightly greater than the presumptive limit of 42 ppm
Note on P39: Lipari, Bernadette: This matches GeOn's 01-24-2023 R3 Supplemantal letter to ACHD
Note on AB39: Lipari, Bernadette: Slightly greater than the presumptive limit of 42 ppm
Note on H50: Lipari, Bernadette: Actual lb/MMBtu = 0.0033 lb/MMBtu VOC (See above ERG calc) CT PTE calc tab uses 0.0030
Note on L50: Lipari, Bernadette: Actual lb/MMBtu = 0.0033 lb/MMBtu VOC (See above ERG calc) CT PTE calc tab uses 0.0030
Note on X50: Lipari, Bernadette: Actual lb/MMBtu = 0.0033 lb/MMBtu VOC (See above ERG calc) CT PTE calc tab uses 0.0030
Note on AB50: Lipari, Bernadette: Actual lb/MMBtu = 0.0033 lb/MMBtu VOC (See above ERG calc) CT PTE calc tab uses 0.0030
Note on I69: Lipari, Bernadette: from the 2006 tvrv - 0.698 lb/mmbtu; 209.4 lb/hr, and 275.2 tpy is from RACT Order 260
Note on N69: Lipari, Bernadette: Cond. V.A.1.e: shall not exceed 96 ppmvd @ 15% O2 = 0.37 lb/MMBtu
Note on J71: Lipari, Bernadette: per 2008 tvrva - this number is from using the allowable 36% capacity factor
Note on I72: Lipari, Bernadette: See note f from emissions summary table from 2006 TVrv and OP#1065009-000-23600