## PTE INPUTS
SPRINGDALE ENERGY, LLC
SPRINGDALE POWER STATION
ANNUAL EMISSIONS CALCULATIONS
INPUT DATA
User Input of Required Parameter Values:
Source | Parameter | Value |  | Comments
Unit No. 1 | Annual Natural Gas Fired | 1807253.5885 | Mcf/yr | Based on HV = 1045 btu/scf
| Max. Annual Heat Input | 1888580 | MMBtu/yr | 424.4 MMBTU/Hr x 4450 hrs/yr
| Annual Operating Hours | 4450 | hrs/yr | TVOP Limit (Combined AE 1 & 2)
| NOx Emission Factor | 41 | lbs/hr | TVOP hourly per-unit limit
| NOx PTE Emissions | 91.225 | tons/yr | Hourly Limit @ 4450 hrs/yr
| SO2 Emission Factor | 0.3 | lbs/hr | TVOP hourly per-unit limit
| SO2 PTE Emissions | 0.6675 | tons/yr | Hourly Limit @ 4450 hrs/yr
| CO2 Emission Factor | 110 | lbs/MMBtu | AP-42, Table 3.1-2a
| CO2 PTE Emissions | 103871.9 | tons/yr | AP-42 EF @ 4450 hrs/yr
| PM/PM10 Emission Factor | 6.6 | lbs/hr | TVOP hourly per-unit limit
| PM/PM10 PTE Emissions | 14.685 | tons/yr | Hourly Limit @ 4450 hrs/yr
| Condensable PM Emission Factor | 0.0047 | lbs/MMBtu | AP-42, Table 3.1-2a
| Condensable PM PTE Emissions | 4.4382 | tons/yr | AP-42 EF @ 4450 hrs/yr
| VOC Emission Factor | 5 | lbs/hr | TVOP hourly per-unit limit
| VOC PTE Emissions | 11.125 | tons/yr | Hourly Limit @ 4450 hrs/yr
| CO Emission Factor | 57 | lbs/hr | TVOP hourly per-unit limit
| CO PTE Emissions | 126.825 | tons/yr | Hourly Limit @ 4450 hrs/yr
| Formaldehyde Emission Factor | 1.4 | lbs/hr | TVOP hourly per-unit limit
| Formaldehyde PTE Emissions | 3.115 | tons/yr | Hourly Limit @ 4450 hrs/yr
Unit No. 2 | Annual Natural Gas Fired | 1807253.5885 | Mcf/yr | Based on HV = 1045 btu/scf
| Max. Annual Heat Input | 1888580 | MMBtu/yr | 424.4 MMBTU/Hr x 4450 hrs/yr
| Annual Operating Hours | 4450 | hrs/yr | TVOP Limit (combined AE 1 & 2)
| NOx Emission Factor | 41 | lbs/hr | TVOP hourly per-unit limit
| NOx PTE Emissions | 91.225 | tons/yr | Hourly Limit @ 4450 hrs/yr
| SO2 Emission Factor | 0.3 | lbs/hr | TVOP hourly per-unit limit
| SO2 PTE Emissions | 0.6675 | tons/yr | Hourly Limit @ 4450 hrs/yr
| CO2 Emission Factor | 110 | lbs/MMBtu | AP-42, Table 3.1-2a
| CO2 PTE Emissions | 103871.9 | tons/yr | Ap-42 EF @ 4450 hrs/yr
| PM/PM10 Emission Factor | 6.6 | lbs/hr | TVOP hourly per-unit limit
| PM/PM10 PTE Emissions | 14.685 | tons/yr | Hourly Limit @ 4450 hrs/yr
| Condensable PM Emission Factor | 0.0047 | lbs/MMBtu | AP-42, Table 3.1-2a
| Condensable PM PTE Emissions | 4.4382 | tons/yr | AP-42 EF @ 4450 hrs/yr
| VOC Emission Factor | 5 | lbs/hr | TVOP hourly per-unit limit
| VOC PTE Emissions | 11.125 | tons/yr | Hourly Limit @ 4450 hrs/yr
| CO Emission Factor | 57 | lbs/hr | TVOP hourly per-unit limit
| CO PTE Emissions | 126.825 | tons/yr | Hourly Limit @ 4450 hrs/yr
| Formaldehyde Emission Factor | 1.4 | lbs/hr | TVOP hourly per-unit limit
| Formaldehyde PTE Emissions | 3.115 | tons/yr | Hourly Limit @ 4450 hrs/yr
Source | Parameter | Value |  | Comments
Unit No. 3 | Annual Natural Gas Fired | 17553531.1005 | Mcf/yr | Based on HV = 1045 btu/scf
| Max. Annual Heat Input | 18343440 | MMBtu/yr | 2094 MMBTU/Hr x 8760 Hrs/yr
| Annual Operating Hours | 8760 | hrs/yr | Maximum hours per year (non-leap year)
| NOx Emission Factor | 20 | lbs/hr | TVOP hourly per-unit limit
| NOx PTE Emissions | 87.6 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| CO Emission Factor | 48 | lbs/hr | TVOP hourly per-unit limit
| CO PTE Emissions | 210.24 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| SO2 Emission Factor | 5.7 | lbs/hr | TVOP hourly per-unit limit
| SO2 PTE Emissions | 24.966 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| PM/PM10 Emission Factor | 19 | lbs/hr | TVOP hourly per-unit limit
| PM/PM10 PTE Emissions | 83.22 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| VOC Emission Factor | 3.8 | lbs/hr | TVOP hourly per-unit limit
| VOC PTE Emissions | 16.644 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| CO2 Emission Factor | 246448 | lbs/hr | TPU Spec Sheet @ -5o F (worst-case)
| CO2 PTE Emissions | 1079442.24 | tons/yr | TPU Spec Sheet factor @ 8760 hrs/yr
| NH3 Emission Factor | 28 | lb/hr | TVOP hourly per-unit limit
| NH3 PTE Emissions | 122.64 | tons/yr | Hourly limit @ 8760 hrs
| Formaldehyde Emission Factor | 0.68 | lb/hr | TVOP hourly per-unit limit
| Formaldehyde PTE Emissions | 2.9784 | tons/yr | Hourly limit @ 8760 hrs
| Condensable PM Emission Factor | 0.021 | lb/MMBtu | Stack Test August 2012
| Condensable PM PTE Emissions | 192.6061 | tons/yr | Stack Test Results @ 8760 hrs/yr
| Sulfuric Acid Mist Emission Factor | 0.685 | lbs/hr | TVOP hourly per-unit limit
| Sulfuric Acid Mist PTE Emissions | 3.0003 | tons/yr | Hourly limit @ 8760 hrs
Unit No. 4 | Annual Natural Gas Fired | 17553531.1005 | Mcf/yr | Based on HV = 1045 btu/scf
| Max. Annual Heat Input | 18343440 | MMBtu/yr | 2094 MMBTU/Hr x 8760 Hrs/yr
| Annual Operating Hours | 8760 | hrs/yr | Maximum hours per year (non-leap year)
| NOx Emission Factor | 20 | lbs/hr | TVOP hourly per-unit limit
| NOx PTE Emissions | 87.6 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| CO Emission Factor | 48 | lbs/hr | TVOP hourly per-unit limit
| CO PTE Emissions | 210.24 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| SO2 Emission Factor | 5.7 | lbs/hr | TVOP hourly per-unit limit
| SO2 PTE Emissions | 24.966 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| PM/PM10 Emission Factor | 19 | lbs/hr | TVOP hourly per-unit limit
| PM/PM10 PTE Emissions | 83.22 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| VOC Emission Factor | 3.8 | lbs/hr | TVOP hourly per-unit limit
| VOC PTE Emissions | 16.644 | tons/yr | Hourly limit @ 8760 (no SU/SD)
| CO2 Emission Factor | 246448 | lbs/hr | TPU Spec Sheet @ -5o F (worst-case)
| CO2 PTE Emissions | 1079442.24 | tons/yr | TPU Spec Sheet factor @ 8760 hrs/yr
| NH3 Emission Factor | 28 | lb/hr | TVOP hourly per-unit limit
| NH3 PTE Emissions | 122.64 | tons/yr | Hourly limit @ 8760 hrs
| Formaldehyde Emission Factor | 0.68 | lb/hr | TVOP hourly per-unit limit
| Formaldehyde PTE Emissions | 2.9784 | tons/yr | Hourly limit @ 8760 hrs
| Condensable PM Emission Factor | 0.023 | lb/MMBtu | Stack Test August 2012
| Condensable PM PTE Emissions | 210.9496 | tons/yr | Stack Test Results @ 8760 hrs/yr
| Sulfuric Acid Mist Emission Factor | 0.685 | lbs/hr | TVOP hourly per-unit limit
| Sulfuric Acid Mist PTE Emissions | 3.0003 | tons/yr | Hourly limit @ 8760 hrs
All Units | Natural Gas Average Heating Value | 1045 | BTU/scf | PGADs HHV - CY2013 Average
Misc | TVOP 0580 Renewal |  | PTE CALCULATIONS
* Reminder: make sure to include startup/shutdown emissions to these totals
[5 empty] | Annual Hours No. 2 Oil Fired | hours/year
[5 empty] | Annual No. 2 Oil Fired | gal/yr
[5 empty] | Annual Hours No. 2 Oil Fired | hours/year
[5 empty] | Annual No. 2 Oil Fired | gal/yr
[5 empty] | Annual Hours No. 2 Oil Fired | hours/year
[5 empty] | Annual No. 2 Oil Fired | gal/yr
Total Annual Fuel Use :
[5 empty] | Annual Kerosene Fired | 200 | gal/yr
Avg. Annual Hours of Operation for:
[5 empty] | 100 kBtu/hr Heaters |  | avg hours/year/heater
[5 empty] | 150 kBtu/hr Heaters |  | avg hours/year/heater
[5 empty] | 320 kBtu/hr Heaters |  | avg hours/year/heater
Misc | Year (for Headers) | PTE CALCULATIONS |  |  | 350 kBtu/hr Heaters |  | avg hours/year/heater
| Date | 2026-05-13
1995 EMISSIONS SUMMARY
0
PTE CALCULATIONS EMISSIONS SUMMARY
TRUE
0

## Typ
2026-05-13
SPRINGDALE ENERGY, LLC
SPRINGDALE POWER STATION
PTE CALCULATIONS EMISSIONS SUMMARY
UNITS 1&2 and 3,4 & 5: ANNUAL CRITERIA AIR POLLUTANT EMISSIONS
Natural Gas Usage Characteristics
| UNIT NO. 1 |  | UNIT NO. 2 |  | UNIT NO. 3 |  | UNIT NO. 4
| Natural Gas |  | Natural Gas |  | Natural Gas |  | Natural Gas
Yearly Qty. Fuel Burned | 1807.2536 | MMcf | 1807.2536 | MMcf | 17553.5311 | MMcf | 17553.5311 | MMcf
Yearly Amt. Heat Input | 1888580 | MMBtu | 1888580 | MMBtu | 18343440 | MMBtu | 18343440 | MMBtu
Calculated Btu/scf | 1045 | Btu/scf | 1045 | Btu/scf | 1045 | Btu/scf | 1045 | Btu/scf

## HAPs Factors (hidden)
SPRINGDALE ENERGY, LLC
SPRINGDALE POWER STATION
PTE CALCULATIONS EMISSIONS SUMMARY
UNITS 1 & 2 AND 3, 4 & 5: ANNUAL TRACE AIR POLLUTANT EMISSION FACTORS
(Sh. 1 of 2)
Natural Gas Characteristics
| PARAMETER | Emission Factors
(lb/MMBtu )
| TRACE ELEMENTS | (a) | (b) | (c) | (d) | (e) | (f) | (g) | (h)
| 1,3-Butadiene | - | 4.3e-07 | - | - | - | - | - | -
| Acetaldehyde | - | 4e-05 | - | - | - | - | - | -
| Acrolein | - | 6.4e-06 | - | - | - | - | - | -
| Benzene | - | 1.2e-05 | - | - | - | - | - | -
| Ethylbenzene | - | 3.2e-05 | - | - | - | - | - | -
| Formaldehyde | - |  | 0.68 | 3.8 | 0.000896 | 0.000902
| Naphthalene | - | 1.3e-06 | - | - | - | - | - | -
| PAH | - | 2.2e-06 | - | - | - | - | - | -
| Propylene Oxide | - | 2.9e-05 | - | - | - | - | - | -
| Toluene | - | 0.00013 | - | - | - | - | - | -
| Xylenes | - | 6.4e-05 | - | - | - | - | - | -
| Methane | - | 0.0086 | - | - |  |  |  | -
| Sulfuric Acid Mist | - | - | 0.0002 | 0.0003 | - | - | - | -
| Ammonia | - | - |  |  | - | - | 28 | 83.22
| Polycyclic Organic Matter (POM) | 4.38e-06 | - | - | - | - | - | - | -
FOOTNOTES:
(b) | Emissions factors for stationary gas tubines, AP-42 Table 3.1-3 and Table 3.1-2a
(c) | H2SO4 emission factor from 7/14/03 stack testing @ Unit #3
Formaldehyde Emission factor from 8/15/2012 stack testing @ Unit #3
(d) | H2SO4 emission factor from 7/14/03 stack testing @ Unit #4
Formaldehyde Emission factor from 8/15/2012 stack testing @ Unit #4
(e) | Formaldehyde Emission factor from 6/5/2000 stack testing @ Units #1
(f) | Formaldehyde Emission factor from 6/5/2000 stack testing @ Units #2
(g) | NH3 emission factor from 8/15/12 stack testing @ Unit #3
(h) | NH3 emission factor from 8/15/12 stack testing @ Unit #4

## Typ_2
SPRINGDALE ENERGY, LLC
SPRINGDALE POWER STATION
PTE CALCULATIONS EMISSIONS SUMMARY
PTE - GHG & CRITERIA AIR POLLUTANT EMISSIONS
PTE Emission Factors
|  | UNIT NOs. 1 & 2 |  |  | UNIT NO. 3 |  |  | UNIT NO. 4
Pollutant |  | Natural Gas/Oil |  |  | Natural Gas |  |  | Natural Gas
NOx |  | 41 | lbs/hr | ( c)(f) | 20 | lbs/hr | (c) | 20 | lbs/hr | (c)
CO |  | 57 | lbs/hr | ( c)(f) | 48 | lbs/hr | (c) | 48 | lbs/hr | (c)
SO2 |  | 0.3 | lbs/hr | ( c)(f) | 5.7 | lbs/hr | (c) | 5.7 | lbs/hr | (c)
PM* |  | 6.6 | lbs/hr | ( c)(f) | 19 | lbs/hr | (c) | 19 | lbs/hr | (c)
PM10* |  | 6.6 | lbs/hr | ( c)(f) | 19 | lbs/hr | (c) | 19 | lbs/hr | (c)
PM2.5* |  | 6.6 | lbs/hr |  | 19 | lbs/hr |  | 19 | lbs/hr
PMCOND |  | 0.0047 | lbs/MMBtu | (a) | 0.021 | lbs/MMBtu | (d) | 0.023 | lbs/MMBtu | (d)
CH4 |  | 0.002 | lbs/MMBtu | (b) | 0.002 | lbs/MMBtu | (b) | 0.002 | lbs/MMBtu | (b)
N2O |  | 0.0002 | lbs/MMBtu | (b) | 0.0002 | lbs/MMBtu | (b) | 0.0002 | lbs/MMBtu | (b)
CO2 |  | 110 | lbs/MMBtu | (b) | 246448 | lbs/hr | (e) | 246448 | lbs/hr | (e)
VOCs* |  | 5 | lbs/hr | ( c)(f) | 3.8 | lbs/hr | (c) | 3.8 | lbs/hr | (c)
Ammonia |  |  |  |  | 28 | lbs/hr | (c) | 28 | lbs/hr | (c)
H2SO4 Mist |  |  |  |  | 0.685 | lbs/hr | (c) | 0.685 | lbs/hr | (c)
Heat Input (MMBtu) |  | 1888580 |  |  | 18343440 |  |  | 18343440
Hours of Operation |  | 4450 |  |  | 8760 |  |  | 8760
*Does not include SU/SD for Units 3/4; these emissions are accounted for in tons/yr PTE Emissions below
PTE Emissions (tons/yr)
|  | UNIT NOs. 1 & 2 Combined |  |  | UNIT NO. 3 |  |  | UNIT NO. 4 |  |  | Facility
Pollutant |  | Natural Gas/Oil |  |  | Natural Gas |  |  | Natural Gas |  |  | Total
NOx |  | 98 |  |  | 87.6 |  |  | 87.6 |  |  | 273.2
CO |  | 115 |  |  | 210.24 |  |  | 210.24 |  |  | 535.48
SO2 |  | 6 |  |  | 24.966 |  |  | 24.966 |  |  | 55.932
PM |  | 17 |  |  | 83.2754 |  |  | 82.1959 |  |  | 182.4712
PM10 |  | 17 |  |  | 83.2754 |  |  | 82.1959 |  |  | 182.4712
PM2.5 |  | 17 |  |  | 83.2754 |  |  | 82.1959 |  |  | 182.4712
PMCOND |  | 4.4382 |  |  | 192.6061 |  |  | 210.9496 |  |  | 407.9938
CH4 |  | 1.8886 |  |  | 18.3434 |  |  | 18.3434 |  |  | 38.5755
N2O |  | 0.18886 |  |  | 1.8343 |  |  | 1.8343 |  |  | 3.8575
CO2 |  | 103871.9 |  |  | 1079442.24 |  |  | 1079442.24 |  |  | 2262756.38
VOC's |  | 10 |  |  | 25 |  |  | 23 |  |  | 58
Ammonia |  |  |  |  | 122.5 |  |  | 122.5 |  |  | 245
H2SO4 Mist |  |  |  |  | 3.0003 |  |  | 3.0003 |  |  | 6.0006
FOOTNOTES:
(a) | Condensable PM emission factor for Natural Gas taken from EPA AP-42 Table3.1-2A, Combustion Turbines
(b) | GHG factors taken from 40 CFR 98, Subpart C, Tables C-1 and C-2, converted to lbs/MMBtu
(c) | Installation Permit & Title V Operating Permit #0580 limits
(d) | Stack Test Results
(e) | TPU Spec Sheet @ - 5 degrees F
(f) | Installation Permit 0580-I001 limits for fuel oil: SO2 = 22.5 lbs/hr; NOx = 71 lbs/hr; CO = 6 lbs/hr; PM/PM10 = 17 lbs/hr; VOCs = 1 lb/hr @ 450 hrs/yr max

## HAPs
SPRINGDALE ENERGY, LLC
SPRINGDALE POWER STATION
HAPs PTE Calculations
|  |  |  | 1888580 | 1888580 | 18343440 | 18343440
|  | Combustion |  | PTE ANNUAL
|  | Turbine |  | EMISSIONS
POLLUTANT |  | Natural Gas |  | (ton/yr)
HAP |  | (lb/MMBtu) |  | UNIT NO 1 | UNIT NO. 2 | UNIT NO. 3 | UNIT NO. 4 | Total
1,3-Butadiene |  | 4.3e-07 | (a) | 0.00040604 | 0.00040604 | 0.0039438 | 0.0039438 | 0.0086998
Acetaldehyde |  | 4e-05 | (a) | 0.037772 | 0.037772 | 0.36687 | 0.36687 | 0.80928
Acrolein |  | 6.4e-06 | (a) | 0.0060435 | 0.0060435 | 0.058699 | 0.058699 | 0.12948
Benzene |  | 1.2e-05 | (a) | 0.011331 | 0.011331 | 0.11006 | 0.11006 | 0.24278
Ethylbenzene |  | 3.2e-05 | (a) | 0.030217 | 0.030217 | 0.2935 | 0.2935 | 0.64742
Formaldehyde |  | See footnotes | (b)( c) | 1.65 | 1.65 | 2.85 | 2.85 | 9
Naphthalene |  | 1.3e-06 | (a) | 0.0012276 | 0.0012276 | 0.011923 | 0.011923 | 0.026302
PAH |  | 2.2e-06 | (a) | 0.0020774 | 0.0020774 | 0.020178 | 0.020178 | 0.04451
Propylene Oxide |  | 2.9e-05 | (a) | 0.027384 | 0.027384 | 0.26598 | 0.26598 | 0.58673
Toluene |  | 0.00013 | (a) | 0.12276 | 0.12276 | 1.1923 | 1.1923 | 2.6302
Xylenes |  | 6.4e-05 | (a) | 0.060435 | 0.060435 | 0.58699 | 0.58699 | 1.2948
[6 empty] | Total HAPs |  | 15.4202
FOOTNOTES:
(a) | Emission factor taken from AP-42, Table 3.1-3 (4/00).
(b) | Formaldehyde Emissions limit for Unit nos 1 &2 is 3.3 tons/yr combined.
(c) | Formaldehyde Emissions limit for Unit nos. 3 & 4 is 5.7 tons/yr.
Annual Units 1 & 2 maximum per-unit heat input calculated as 424.4 MMBtu/hr x 4,450 hours/yr = 1,888,580 MMBtu/Year
Annual Units 3 & 4 maximum per-unit heat input calculated as 2,094 MMBtu/hr x 8,760 hours/yr = 18,343,531 MMBtu/Year

## NH3 tank
Springdale Energy, LLC
Springdale Power Station
Units AE 3, 4 & 5
ACHD Permit # 0580-I002a
Aqueous Ammonia Usage
MAX Throughput |  |  |  | 600000 | Gallons
% THROUGHPUT
Dec-Feb | 25%
Mar-May | 25%
Jun-Aug | 25%
Sep-Nov | 25%
Note: USEPA Tanks 4.09b used to estimate NH3 Emissions
Standing Loses | = | 477
Working Loses | = | 818.6
Tanks Total Loses | = | 1295.6 | lbs/yr
|  | 0.6478 | tpy

## Cooling Tower
Springdale Energy, LLC
Springdale Power Station
Units AE 3, 4 & 5
ACHD Permit # 0580-I002a
COOLING TOWER EMISSION PTE CALCULATIONS (AP-42 Table 13.4-1)
Cooling Tower has two pumps rated at 43,860 gpm each (combined total 87,720 gpm)
Permit Limit for TDS is 3000 ppm (mg/L)
TVOP Limit | 3000 | mg/L | = | 0.024978 | lb/gal
Design Cooling Tower Drift Rate* |  |  | = | 0.0005% | (installation permit application)
Cooling Tower Circulating Water Flow |  |  | = | 87720 | gpm
AP-42 Emission Factor* |  |  | = | 0.02% | table 13.4-1 (1/95)
Estimated Control Efficiency |  |  | = | 97.5% | H.E. Mist Eliminator (calculated)
* total liquid drift as a percentage of circulating water flow
note: cooling tower only operates when CCCT's are in operation
maximum operating hours for COOLING TOWER |  |  | = | 8760 | hrs/yr
total circulating water flow |  |  | = | 46105632000 | gallons
Total Liquid Drift (uncontrolled) |  |  | = | 9221126.4 | gallons | AP-42
Total Solids contained in Drift (PM/PM10/PM2.5) |  |  | = | 230325.0515 | lbs/yr | uncontrolled
Total Liquid Drift (controlled) |  |  | = | 230528.16 | gallons
Annual Average Cooling Tower TDS |  |  | = | 0.024978 | lb/gal | (Limit)
Total Solids contained in Drift (PM/PM10/PM2.5) |  |  |  | 5758.1263 | lbs/yr | controlled (H.E. mist eliminator)
|  |  |  | 2.8791 | tons/yr | PM emissions
assume PM = PM10 = PM2.5

## SU-SD
Springdale Energy, LLC
Springdale Power Station
AE 3, 4, 5
Start Up/Shutdown PTE Emissions
July 2003 Stack Tests - Startup Emission Rates
Unit | cold start | warm start | hot start |  | SU/SD Events/Year | Unit 3 | Unit 4
[5 empty] | Cold Starts | 52 | 52
[5 empty] | Warm Starts | 52 | 52
| VOCs (lbs/start)* |  |  |  | Hot Starts | 52 | 52
Unit #3 | 181.21 | 94.15 | 78.05
Unit #4 | 135.76 | 68.9 | 65.42 |  | Max SU/SD Hrs/Event* | Unit 3 | Unit 4
[5 empty] | Cold Starts | 6.25 | 6.25
| PM/PM10 (lbs/start)* |  |  |  | Warm Starts | 3.75 | 3.75
Unit #3 | 61.66 | 37.26 | 21.96 |  | Hot Starts | 2.5 | 2.5
Unit #4 | 39.01 | 24.68 | 15.67 |  | *Title V Permit Limits
*Data from IP 0580-I002 application
MAX PTE SU/SD Emissions (tons/yr) |  |  |  |  | Max SU/SD hrs/yr | 325
Unit | Start Up Type | VOCs | PM/PM10 |  | Max non-SU/SD hrs/yr | 8435
3 | Cold | 4.7115 | 1.6032 | SU/SD Totals
| Warm | 2.4479 | 0.96876 | U3 VOC Sum
| Hot | 2.0293 | 0.57096 | 9.1887
4 | Cold | 3.5298 | 1.0143
| Warm | 1.7914 | 0.64168 | U4 VOC Sum
| Hot | 1.7009 | 0.40742 | 7.0221
U3 PM Sum
3.1429
U4 PM Sum
2.0634

## SPDL Permit Limits Summary
| SPDL lb/hr limits | [10 empty] | SPDL ton/year limits | [5 empty] | Table VIII-2 in IP5 Emissions for Units 3&4, cooling tower and ammonia tank |  | Combined Emissions Table in rv5 (TSD for IP5) Units 1-4, cooling tower and ammonia tank
Pollutant | Unit 1 and 2 Natural Gas lb/hr each | Unit 1 and 2 Fuel Oil lb/hr each | Unit 1 and 2 Natural Gas lb/hr combined | Unit 1 and 2 Fuel Oil lb/hr combined | Unit 3 and 4 lb/hr each | Unit 3 and 4 lb/hr combined | Cooling Tower | Ammonia tank | EG01 and EG02 lb/hr each | EG01 and EG02 lb/hr total | Total SPDL Combined1 lb/hr | Unit 1 and 2 | Unit 3 and 4 | Cooling Tower | Ammonia Tank | EG01 and EG02 | Total SPDL Combined Annual ton/year | Hourly Emission Limit lb/hr total | Annual Emissions tpy | Combined tons/year
Particulate Matter (PM) | 6.6 | 17 | 13.2 | 34 | 19 | 38 | 1.12 |  | 0.08 | 0.16 | 73.28 | 17 | 166 | 4.9 |  | 0.04 | 187.94 | 39.12 | 170.9 | 187.9
Particulate Matter (PM10) | 6.6 | 17 | 13.2 | 34 | 19 | 38 | 1.12 |  | 0.08 | 0.16 | 73.28 | 17 | 166 | 4.9 |  | 0.04 | 187.94 | 39.12 | 170.9 | 187.9
Sulfur oxides (SOX) | 0.3 | 22.5 | 0.6 | 45 | 5.7 | 11.4 |  |  | 0.018 | 0.036 | 56.436 | 6 | 53 |  |  | 0.01 | 59.01 | 11.4 | 53 | 59
Nitrogen oxides (NOX) | 41 | 71 | 82 | 142 | 20 | 40 |  |  | 24.89 | 49.78 | 231.78 | 98 | 210 |  |  | 12.45 | 320.45 | 40 | 210 | 308
Carbon monoxide (CO) | 57 | 6 | 114 | 12 | 48 | 96 |  |  | 0.843 | 1.686 | 211.686 | 115 | 550 |  |  | 0.42 | 665.42 | 96 | 550 | 665
Volatile organic compounds (VOC) | 5 | 1 | 10 | 2 | 3.8 | 7.6 |  |  | 0.401 | 0.802 | 18.402 | 10 | 48 |  |  | 0.2 | 58.2 | 7.6 | 48 | 58
Sulfuric Acid Mist |  |  |  |  | 0.685 | 1.37 |  |  |  |  | 1.37 |  | 6 |  |  |  | 6 | 1.37 | 6 | 6
Formaldehyde | 1.4 |  | 2.8 |  | 0.68 | 1.36 |  |  |  |  | 4.16 | 3.3 | 5.7 |  |  |  | 9 | 1.36 | 5.7 | 9
Ammonia |  |  |  |  | 28 | 56 |  | 0.1484 |  |  | 56.1484 |  | 245 |  | 0.65 |  | 245.65 | 56.1484 | 245.65 | 245.65
1. For the Total SPDL combined lb/hr for Unit 1 and 2 the worst case between natural gas and fuel oil is used.

## G02
Springdale Power Station Emission Calculations: Fire Pump Engine
Engine Rating
[6 empty] | 265 | bhp
[6 empty] | 14.2 | gal/hr
Clarke Model JDFP-06WA Fire Pump rated at 265 BHP | [5 empty] | 138000 | diesel Btu/gal
[6 empty] | 1.9596 | MMBtu/hr
Criteria Pollutants -Manufacturer Calculations
Pollutant | Emission Factor (g/HP-hr)* | Emission Factor (lbs/HP-hr) | Operating Hours | lbs/hr | tons/yr
NOX | 6.7 | 0.014771 | 500 | 3.9143 | 0.97858
CO | 0.29 | 0.00063934 | 500 | 0.16943 | 0.042356
SO2 | 0.67 | 0.0014771 | 500 | 0.39143 | 0.097858
PM/PM10 | 0.07 | 0.00015432 | 500 | 0.040896 | 0.010224
VOC | 0.23 | 0.00050706 | 500 | 0.13437 | 0.033593
*Based on Manufacturer data
HAP Calculations
HAP | Emission Factor* (lb/MMBtu) | Operating Hours | lbs/hr | tons/yr
1,3-butadiene | 3.91e-05 | 500 | 7.662e-05 | 1.9155e-05
Acetaldehyde | 0.000767 | 500 | 0.001503 | 0.00037575
Acrolein | 9.25e-05 | 500 | 0.00018126 | 4.5316e-05
Benzene | 0.000933 | 500 | 0.0018283 | 0.00045708
Formaldehyde | 0.00118 | 500 | 0.0023123 | 0.00057808
PAH | 0.000168 | 500 | 0.00032921 | 8.2303e-05
Toluene | 0.000409 | 500 | 0.00080148 | 0.00020037
Xylene | 0.000285 | 500 | 0.00055849 | 0.00013962
*AP-42 Table 3.3-2
GHG Calculations
GHG | Emission Factor* (lb/MMBtu) | Operating Hours | lbs/hr | tons/yr
CO2 | 163.0537 | 500 | 319.52 | 79.88
CH4 | 0.0066139 | 500 | 0.012961 | 0.0032401
N2O | 0.0013228 | 500 | 0.0025921 | 0.00064803
*40 CFR Part 98 Table C-1 and C-2.

## EGs
Springdale Energy, LLC
EG01 and EG02
Criteria and GHG Potential Emissions
Caterpillar C32 -- 1,250 EKW Nominal
Constants
32.1 | lb/lb-mol; sulfur molecular weight
64.1 | lb/lb-mol; SO2 molecular weight
453.6 | g/lb
2.2046 | lb/kg
2000 | lb/ton
0.7457 | kW/bhp
7 | lb/gal; Diesel fuel density, calculated from engine data sheet
0.137 | MMBtu/gal; nominal heat content of diesel, AP-42, Appendix A
2.5 | %; fraction of NMHC in NOx + NMHC, from data in AP-42 Table 3.4-1 (10/96)
73.96 | kg/MMBtu; CO2 for Diesel Fuel Combustion; 40 CFR 98 Table C1
0.003 | kg/MMBtu; CH4 for Diesel Fuel Combustion; 40 CFR 98 Table C2
0.0006 | kg/MMBtu; N2O for Diesel Fuel Combustion; 40 CFR 98 Table C2
1 | ton CO2e per ton of CO2; global warming potential, 40 CFR 98, Table A-1
25 | ton CO2e per ton of CH4; global warming potential, 40 CFR 98, Table A-1
298 | ton CO2e per ton of N2O; global warming potential, 40 CFR 98, Table A-1
Design Values
2 | number of engine-generators
1821 | bhp; engine power rating at 100% load
0.336 | lb/bhp-hr; brake-specific fuel consumption rate at 100% load
0.0015 | wt %; sulfur content of ultra-low sulfur diesel
500 | hr/yr; maximum operating hours, each engine-generator1
Intermediate Calculated Values
611.856 | lb/hr; fuel consumption rate, calculated
87.408 | gal/hr; fuel consumption rate, calculated
Criteria Pollutant Emission Rates
| NOX | VOC2 | CO | PM | PM10 | SO2
lb/hr/unit1 | 24.89 | 0.401 | 0.843 | 0.08 | 0.08 | 0.018
lb/hr total | 49.78 | 0.802 | 1.686 | 0.16 | 0.16 | 0.036
ton/yr/unit | 6.2225 | 0.10025 | 0.21075 | 0.02 | 0.02 | 0.0045
ton/yr total | 12.445 | 0.2005 | 0.4215 | 0.04 | 0.04 | 0.009
Springdale Energy, LLC
EG01 and EG02
Criteria and GHG Potential Emissions (cont.)
Caterpillar C32 -- 1,250 EKW Nominal
Greenhouse Gasses Combined Emission Rates
| CO22 | CH4 | N2O | CO2e
lb/hr/unit | 1917 | 0.0792 | 0.01584 | 1923.7003
lb/hr total | 3834 | 0.1584 | 0.03168 | 3847.4007
ton/yr total | 958.5 | 0.0396 | 0.00792 | 961.8502
Notes
1. Emissions rates are based on the permit limit in Installation Permit No. 0580-I004.
2. CO2 emission rate provided by engine manufacturer for 100 percent load condition.

## EGsHAPs
Springdale Energy, LLC
EG-01 and EG-02
Toxic and Hazardous Emissions
Caterpillar C32 -- 1,250 EKW Nominal
Design Values
2 | number of engine-generators
87.4 | gal/hr; fuel consumption at 100% load manufacturer data, C32 Caterpillar, 1829 BHP rating
0.137 | MMBtu/gal; nominal heat content of diesel, AP-42, Appendix A
11.9738 | MMBtu/hr; heat input capacity, calculated
500 | hr/yr; maximum operating hours, each engine-generator1
100 | hr/yr; maximum expected actual operating hours, each engine-generator
TAP/HAP2 Emission Factors (AP-42, Table 3.4-3, (10/96))
TAP/HAP |  | lb/MMBtu | lb/unit-hr | lb/yr, total |  | ton/yr, total
|  |  |  | Potential | Actual | Potential | Actual
Benzene |  | 0.000776 | 0.0092917 | 9.2917 | 1.8583 | 0.0046458 | 0.00092917
Toluene |  | 0.000281 | 0.0033646 | 3.3646 | 0.67293 | 0.0016823 | 0.00033646
Xylenes |  | 0.000193 | 0.0023109 | 2.3109 | 0.46219 | 0.0011555 | 0.00023109
PAH (total) |  | 0.000212 | 0.0025384 | 2.5384 | 0.50769 | 0.0012692 | 0.00025384
Propylene3 |  | 0.00279 | 0.033407 | 33.4069 | 6.6814 | 0.016703 | 0.0033407
Formaldehyde |  | 7.89e-05 | 0.00094473 | 0.94473 | 0.18895 | 0.00047237 | 9.4473e-05
Acetaldehyde |  | 2.52e-05 | 0.00030174 | 0.30174 | 0.060348 | 0.00015087 | 3.0174e-05
Acrolein |  | 7.88e-06 | 9.4354e-05 | 0.094354 | 0.018871 | 4.7177e-05 | 9.4354e-06
Total TAPs |  | 0.004364 | 0.052253 | 52.2534 | 10.4507 | 0.026127 | 0.0052253
Total HAPs |  | 0.001574 | 0.018847 | 18.8465 | 3.7693 | 0.0094233 | 0.0018847
Notes:
1. See EPA Memorandum from John S. Seitz, Director, Office of Air Quality Planning and Standards (MD-10), “Calculating Potential to Emit (PTE) for Emergency Generators” (Sept. 6, 1995), available at https://www.epa.gov/sites/production/files/2015-08/documents/emgen.pdf.
2. "TAP" = toxic air pollutant; "HAP" = hazardous air pollutant (per 42 U.S.C. 7412(b)(1) and 40 CFR 63 §§ 60-63). TAPs are defined by the ACHD within the document "Policy for Air Toxics Review of Installation Permit Applications," last revised January 9, 2013.
3. Not a listed hazardous air pollutant (HAP); other species listed are defined as HAPs. Propylene is not listed in EPA's Integrated Risk Information System database but is assigned an inhalation Reference Exposure Level by California's Office of Environmental Health Hazard Assessment.

## PTE Appendix
SPRINGDALE ENERGY, LLC
SPRINGDALE POWER STATION
Facility PTE Summary
(Tons/Year)
Emission Source
Criteria Pollutants | Units 1&2 | Unit 3 | Unit 4 | T-2 NH3 Storage | EG01 | EG02 | G02 Emergency Fire Pump | CT-2 Cooling Tower
NOx | 98 | 87.6 | 87.6 |  | 6.2225 | 6.2225 | 0.97858
CO | 115 | 210.24 | 210.24 |  | 0.21075 | 0.21075 | 0.042356
SO2 | 6 | 24.966 | 24.966 |  | 0.0045 | 0.0045 | 0.097858
PM | 17 | 83.2754 | 82.1959 |  | 0.02 | 0.02 | 0.010224 | 2.8791
PM10 | 17 | 83.2754 | 82.1959 |  | 0.02 | 0.02 | 0.010224 | 2.8791
PM2.5 | 17 | 83.2754 | 82.1959 |  |  |  |  | 2.8791
PMCOND | 4.4382 | 192.6061 | 210.9496
VOCs | 10 | 25 | 23 |  | 0.10025 | 0.10025 | 0.033593
Hazardous Air Pollutants
1,3-Butadiene | 0.00081209 | 0.0039438 | 0.0039438 |  |  |  | 1.9155e-05
Acetaldehyde | 0.075543 | 0.36687 | 0.36687 |  | 0 | 0 | 0.00037575
Acrolein | 0.012087 | 0.058699 | 0.058699 |  | 0 | 0 | 4.5316e-05
Benzene | 0.022663 | 0.11006 | 0.11006 |  | 0.0025 | 0.0025 | 0.00045708
Ethylbenzene | 0.060435 | 0.2935 | 0.2935
Formaldehyde | 3.3 | 2.85 | 2.85 |  | 0 | 0 | 0.00057808
Naphthalene | 0.0024552 | 0.011923 | 0.011923
PAH | 0.0041549 | 0.020178 | 0.020178 |  | 0.0005 | 0.0005 | 8.2303e-05
Propylene Oxide | 0.054769 | 0.26598 | 0.26598
Toluene | 0.24552 | 1.1923 | 1.1923 |  | 0.001 | 0.001 | 0.00020037
Xylenes | 0.12087 | 0.58699 | 0.58699 |  | 0.0005 | 0.0005 | 0.00013962
Air Toxics
Sulfuric Acid Mist | 0 | 3.0003 | 3.0003
Ammonia | 0 | 122.5 | 122.5 | 0.6478
Greenhouse Gases
CH4 | 1.8886 | 18.3434 | 18.3434 |  | 0.02 | 0.02 | 0.0032401
N2O | 0.18886 | 1.8343 | 1.8343 |  | 0.004 | 0.004 | 0.00064803
CO2 | 103871.9 | 1079442.24 | 1079442.24 |  | 479.5 | 479.5 | 79.88
*Emissions from Unit 1 not included in total since calcs show each unit operating at the permit limit of 4450 hours (combined U1 & U2)